### INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

# Title:  Draft ExTAG Decision Sheet – Two independent types of protection Gb to meet Ga requirements.

INTRODUCTION

# This document, ExTAG/678/CD, Draft ExTAG Decision Sheet Two independent types of protection Gb to meet Ga requirements. has been prepared by Eurofins, CML, GB and is issued for consideration by ExTAG.

In accordance with OD 035 this document is issued for a six-week comment period.

Please submit comments on this new Draft DS using the comments table, a separate document, by –

2022 07 18

to

Christine Kane

ExTAG Secretariat

| Address: IECEx Secretariat Level 33, Australia Square 264 George Street Sydney NSW 2000 Australia | Contact Details: Tel: +61 2 4628 4690 Fax: +61 2 4627 5285 e-mail: info@iecex.com http://www.iecex.com |
| --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-26 Fourth Edition 2021 IEC 60079-0 Seventh Edition 2017 | Clause: 4.2: IEC 60079-26 Table 15: IEC 60079-0 |  |
| --- | --- | --- |
| Subject: Two independent types of protection Gb to meet Ga requirements. Status of document: Draft | Key words: Ex eb terminals Junction box | Date: 02/06/2022 Originator of proposal: Eurofins CML |
| BACKGROUND: Clause 4 of IEC 60079-26 describes Ex Equipment with two combined Types of Protection to achieve EPL Ga for none intrinsically safe circuits. Clause 4.2 gives examples, including an assembly with only one enclosure as long as the enclosure and cable glands meet the impact test requirements for Group I. QUESTION: Is it possible to use increased safety terminals (certified as an Ex component) inside of a Group I certified junction box and fitted with Group I certificated cable glands to achieve EPL Ga? ANSWER: Yes, provided that the enclosure also meets IEC 60079-0, IP54 enclosure requirements and appropriate creepage and clearances – if a failure of the increased safety terminals, providing two independent types of protection relying on one enclosure. The Group I impact values that the junction box and the cable glands must meet can also be the low impact values (7 Joules) as defined in IEC 60079-0 Table 15 for low risk of impact applications. |