INTERNATIONAL ELECTROTECHNICAL COMMISSION SCHEME FOR CERTIFICATION TO STANDARDS FOR EXPLOSIVE ATMOSPHERES (IECEx SCHEME)

Ex Management Committee, ExMC and

Ex Testing and Assessment Group, ExTAG

Compilation of Comments received concerning document OD 015/V1

Title:	Technical Requirements for IECEx Service Facilities involved in repairs, overhauls and modifications of Ex equipment.

##### Introduction

This document is a compilation of comments received relating to document OD 015/V1.

OD015/V1 was discussed during the ExMC Brdo 2004 Meeting with members suggesting that more time was required to consider the document. The Secretary then proposed, and the meeting agreed, to allow a further period to submit comments, the closing date being 31 December 2004.

Chris Agius

IECEx Secretariat

| Address: IECEx Secretariat SAI Building 286 Sussex Street Sydney 2000 Australia | Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 Email: chris.agius@iecex.com Internet: www.iecex.com |
| --- | --- |

# COMPILATION OF COMMENTS ON COMMITTEE DOCUMENT

| ## Reference number of the Draft ### OD 015/Version 1 | Date of Circulation: 2004 07 |
| --- | --- |
|  | ## Date of issue of CC: 2005 02 |

## Title of the Committee Document: Technical Requirements for IECEx Service Facilities involved in repairs, overhauls and modifications of Ex equipment

The above-mentioned document was circulated to IECEx Member Bodies, ExCBs, Candidate ExCBs, ExTLs and Candidate ExTLs with a request that comments be submitted by 31st December 2004.

## Comments received – CN, DE, NL, RU, US

## ACTION: Referred to IECEx Officers meeting 11 February 2004, where Chairman decided to proceed with issuing a revised draft of IECEx 03 for voting by ExMC and prepare revised draft ODs incorporating comments received.

| IECEx Member Body | Comment No. | Clause/ Subclause/ Section | Paragraph Figure/ Table | Type of comment (General/ Technical/ Editorial) | COMMENTS | Proposed change | OBSERVATIONS OF THE SECRETARIAT on each comment submitted |
| --- | --- | --- | --- | --- | --- | --- | --- |
| NL | 1 |  |  | General | introduce the definition “service” (see OD014 comments) and use this throughout the document |  | Noted |
| US | 2 |  |  | General | (Overall) Is it premature to release OD15 as a defined set of reqts when the next edition of IEC 60079-19 is still under development by TC31 and will not be done until 10-2006? This sets a very concerning precedent to supersede published IEC docs via publishing OD documents. Will the CAB even allow this? And if they do, and this is published, will service facilities have access to it? |  | From the discussions during the Brdo ExMC meeting it was concluded that current edition 60079-19 is used and OD 015 be re-written to be more of a supporting document that provides clarification of any points or gaps contained within 60079-19 US concerns regarding a precedent is noted. |
| NL | 3 | introduction |  | Editorial | introduction -: refers to “this part of IEC 60079”, which is not the case (yet). | It should be deleted from OD015 since it is misleading | Noted |
| NL | 4 | 1 |  | Editorial | Change ”repair,…modification to “servicing” |  | Noted |
| CN | 5 | 2.1 |  | Editorial | In clause 2.1 normative references, add IEC 60079-26. |  | Noted |
| NL | 6 | 2.1 |  | Editorial | delete “this part of IEC 60079” |  | Noted |
| NL | 7 | 2.2.10 |  | Editorial | definition 2.2.10: make sure that this definition is the same as in OD014, section 1.2 |  | Noted |
| NL | 8 | 2.2.12.2 |  | Technical | 2nd paragraph: reference is made to “certification documents”. Please add a definition of “certification documents” to section 2 to avoid any confusion about this. Please note that in Europe, Zone 2 equipment need not be certified and therefore there are no “certification documents”! This gives problems in several clauses of OD015. Perhaps it is better to refer to the “documentation provided by the manufacturer”, which might have been used for third party certification? |  | Agree |
| #### DE | 9 | General Principles 2.3 | (b) | Technical | The requirements in this clause are not as stringent as necessary. Change the text as proposed | In circumstances where the certification documents are not available then the repair or overhaul shall be carried out on the apparatus in accordance with this Operational Document and all other relevant standard(s) of the corresponding type of protection. If other repair or modification techniques are used not in accordance with this Operational Document, then it will be is necessary to ascertain, from the manufacturers, and/or the certification authority, the suitability of the apparatus for continued use in a potentially explosive atmosphere | Agree |
| NL | 10 | 2.3 |  | Technical | last paragraph: please note that in case of modifications such that the function of the equipment and/or the design characteristics (ratings) have changed, the equipment is considered as new equipment and is subject to the requirements of the ATEX directive 94/9/EC in Europe. For Zone 0 and 1 equipment certification is then required, for Zone 2 equipment self-certification by the manufacturer is allowed. In all cases the Service Facility becomes the legal new manufacturer, with all the obligations under the ATEX directive. OD015 may allow these modifications, ATEX however does not allow this without introducing the Service Faclity as the new manufacturer. Implementation of OD015 in the European IECEx Members will result in a national (European) deviation on this matter |  | Noted. We could consider a note to highlight this |
| NL | 11 | 2.5.1 |  | Technical | please note that in Europe it is not required to provide to the user the Ex certificate with the Ex equipment. What always must be provided to the user is the EC Declaration of Conformity and the installation instructions / manual as included in clause 30 of IEC 60079-0 (2004). As a result, many times this requirement of 2.5.1 will not be met. |  | Noted. This is an example of why the word “should” and not “shall” has not been used. |
| NL | 12 | 2.6.1 |  | Technical | first paragraph: question: what is meant with “certification status” in this context? Equipment is certified or not, which can be determined from the marking on the equipment. |  | It is possible that the equipment has been modified outside the provisions of certification |
| NL | 13 | 2.6.1 |  | Technical | 2nd paragraph: question: what is meant with “the repaired/overhauled equipment complies with the certification status agreed with the user”? The user cannot claim certification if it is not marked as such. What is there to agree upon? |  | See comment 11 |
| DE | 14 | 2.6.1.2 | 3rd paragraph | Technical | Manufacturer of such apparatus are audited latest each 18 month. For service facilities the training shall be given not later than each 3 years. The responsibility of the service facilities is according this standard very high (see note of 2.6.1.3) and therefore the training periods have to be reduced. | Appropriate refresher training shall be given from time to time, not longer than at three-year 18 month intervals. | While agreed this needs to align with the new 60079-19 when finalised |
| DE | 15 | Complete standard |  | Editorial | Use for the terms drawings/documents the terms used in OD 005 | Use: schedule drawing related drawing technical documentation manufacturers documents | Agree |
| DE | 16 | 2.6.1.4 | 1st paragraph 2nd sentence | Editorial | Sentence not understandable. Maybe there is a misspelling. |  | Agree to review |
| #### DE | 17 | 2.6.1.4.1 | NOTE 2 | Technical | According 60079-0 Ed. 4 manufacturer are only required to give repair instruction if appropriate. Note 2 as given is this standard leads to the opinion that manufacturer have to give repair instruction in all cases. | NOTE 2: As from Ed 4 IEC 60079-0 manufacturers are required to give Instructions including repair instruction if appropriate. | Agree to review |
| RU | 18 | 2.6.1.4.1 |  | Technical | We propose to add after the heading «General» the following paragraph: «The Service Facility shall have the repair documentation agreed-on with the Certification Body». It will correspond to paragraph 2.6.1.4. of current Russian standard GOST R 51330.18-99 (harmonized with IEC 60079-19-93) . |  | Agree to review |
| DE | 19 | 2.6.1.4.2 | 1st paragraph | Technical | A period of time is no sufficient requirement. See 2.6.1.4.3 where 10 years are required. | The job records of repairs/overhauls shall be retained for a period of time 10 years. as agreed with the User. Retained information shall be adequately controlled to ensure correct retrieval. | Agree |
| DE | 20 | 2.6.1.4.3 | 1st paragraph 1) | Technical | A licence shall be a fundamental requirement. | 1) Details of Repair Licence Scheme providers Quality Assessment Scheme (where a licence is held) | Agree to revise |
| NL | 21 | 2.6.1.4.3 |  | Technical | what is meant with “Certification of Facility Quality Standard including..”. Can’t this be rewritten in simple English? Same for “1) Details of Repair Licence Scheme providers Quality Assessment Scheme…” which is Chinese to me |  | Agree to revise |
| NL | 22 | 2.6.1.4.3 | Item 9 Para 1 | Technical | Register of manufacturer’s drawings: add “and drawings generated by the Service Facility in case of modifications” |  | Agree |
| NL | 23 | 2.6.1.4.3 | Item 4 Para 2 | Technical | Job Records including, item 4): usually a replacement component has no Certificate of Conformity when with component is meant a component according to the definition of 2.2.5. Please use the definition 3.14 of IEC 60079-0 (2004) for Ex-components and make sure that if other components are meant (for example a new door for an Ex d enclosure: the enclosure has been certified as an Ex-component, the door is a non-Ex-component according to the definition of 2.2.5) this is clearly laid down |  | Agree to add “where appropriate” |
| DE | 24 | 2.6.1.5.2 | 1st paragraph | Technical | In other clause of this standard repair instructions are required. In this clause it seems that a parts list is required from the manufacturer. To provide a parts list cannot be an acceptable requirement for the manufacturer. | Parts, which are required by the apparatus specification and certificate documents to be sealed, shall be replaced only by the particular spare part(s) detailed in the parts list repair instruction. | Agree |
| DE | 25 | 2.6.1.6 | 3rd paragraph b) | Technical | In case of issuing a certificate the assessment of an apparatus is restricted to an ExTL and ExCB. This clause gives the service facility the same responsibility as for an ExTLs and ExCBs. This responsibility for the service facility is contents of several clauses in this standard and should be reconsidered. | A repaired apparatus has to be in accordance to the schedule drawings always. | Refer to WG10 |
| NL | 26 | 2.6.1.6 | 3rd paragraph b) | Technical | if the apparatus does not comply anymore with the certification documents (= the construction is not the same as when it was certified), the certification label MUST be removed. In addition, we will certainly not support the repair symbol “R” within an inverted triangle (A.2.2). If apparatus has changed so that it no longer is in compliance with the certification documents, a new certificate must be obtained. In this case, only after having obtained the certificate, the symbol of A.2.1 is written on the serviced apparatus. The use of the R-symbol of A.2.2. is misleading and confusing with the symbol of A.2.1 and MUST therefore be deleted from OD015. |  | To align with the final text for 60079-19 revised edition |
| NL | 27 | 2.6.1.7 |  | Technical | reference is made only to ISO 9000 series, which is an unnecessary limitation. Please add a line like: “It does not preclude the use of other qulaity systems that are compatible with the objectives of ISO 9001”. |  | Agree to revise |
| DE | 28 | 2.6.2.3 | 5th paragraph | Technical | This paragraph is in contradiction to the requirements given in 2.6.1.6 where for the same situation the label has not to be removed. Further see comment to 2.6.1.6 | A repaired apparatus has to be in accordance to the schedule drawings always. | Agree to revise |
| DE | 29 | 2.6.2.3 | 6th paragraph | Technical | The wording “should” is not stringent enough. Use “shall” instead of “should” | In the event of any uncertainty regarding the permissibility, from an explosion-protection safety point of view, of an intended reclamation procedure, the advice of the manufacturer or certifying authority should shall be sought. | Agree |
| CN | 30 | 2.6.3 |  | Technical | In 3.4.1, 4.4, 5.4.1, 6.4.1 and 7.4.1 or in 2.6.3 add: It should, where appropriate, take account of the requirements of the apparatus standard to avoid frictional sparking and electrostatic charging |  | Agree |
| DE | 31 | 2.6.3 | 1st paragraph 1st sentence | Editorial | Misspelling | Please correct | Noted |
| NL | 32 | 3.2.4 | 2nd | General | even with reference to the manufacturer, the apparatus is not certified anymore due to the increase of ratings. A new certificate is necessary |  | Refer to WG10 |
| NL | 33 | 3.2.6.1 |  | Technical | increase of rating> see remark to 3.2.4 |  | Refer to WG10 |
| NL | 34 | 3.2.6.3.1 |  | Technical | a flux test (see 3.3.4) should be added here |  | Refer to WG10 |
| CN | 35 | 3.4.1 |  | Technical | In 3.4.1, 4.4, 5.4.1, 6.4.1 and 7.4.1 or in 2.6.3 add: It should, where appropriate, take account of the requirements of the apparatus standard to avoid frictional sparking and electrostatic charging |  | Agree |
| NL | 36 | 3.4.4 |  | ###### Technical | this is NOT acceptable. Rewinding for another voltage results in a new apparatus, which MUST be certified. Reference made to the manufacturer is not sufficient. Same for rewinding for a different speed: unacceptable |  | Agree if new voltage is outside limits of certification |
| DE | 37 | 4 | General | ###### Technical | Unfortunately the good old days are gone where the i.s. circuit was realized with a safety fuse, zener diodes and resistor.... Nowadays thyristor circuits as well as voltage regulators are being used beside the well-known voltage limiters consisting of zener diodes. Also the use of switched-mode power supplies (SMPS) leads to an increasing number of safety critical components. Also the concepts of the installations inside the hazardous area have been changed. The individual devices are being installed more and more directly inside the hazardous areas such as Zone 0, Zone 1 or Zone 2. Therefore not only individual components inside the devices are to be considered as safety critical components. These devices contain sometimes up to 700 and more components, which are all to be considered as critical electrical components. Besides the named critical electrical components in this standards there are many other critical electrical components. Many of these components are selected. Such components can only be replaced by components, which are obtained from the manufacturer of the apparatus. A service facility is not able to recognize these components. This makes the decision for the service facility impossible, which of the component are safety relevant or not. Further individual devices of a Bus system cannot be brought in function without other devices, nearly the complete system is necessary. The documents of such apparatus include so much knowledge and experience of the manufacturers that no manufacturer will give the schedule drawings or the related drawings to a service facility. The possibility for the service facility to repair such apparatus is restricted to the change of a fuse. The legal responsibility of the apparatus manufacturer will never lead to support a service facility to repair such complicated apparatus in type of protection “i”. The manufacturers document of such apparatus are marked with “Repair and overhaul is not permissible” | Delete the complete type of protection “i” in this standard or as a minimum type of protection “ia” and “ib” | While in general agreement the inclusion of i.s is for the situation where the service facility holds all necessary manufacturing documents and is operating in agreement with the manufacturer. This may need to be clarified. |
| DE | 38 | 4.1 | Note | Technical | Type of protection “ic“ is missing. A clear differentiation of intrinsically safe apparatus and associated apparatus is missing. | Please correct the note. | Noted |
| DE | 39 | 4.2.2 |  | Technical | Not only the cable entries also the cable glands are important for the safety of the apparatus. | Add the following: Cable glands shall be replaced by adequate and certified types only. The permissible ambient temperature of the apparatus has to be considered. | Agree to review |
| NL | 40 | 4.2.2 |  | Technical | what is considered as “special entries”? |  | Agree to review |
| DE | 41 | 4.2.4 | 2nd dash | Editorial/ Technical | The wording “sweated” is unclear. | Please correct. | Noted |
| DE | 42 | 4.2.4 | 3rd dash | Technical |  | Add the following: - if a printed circuit board track is repaired by using a wire an equal cross-section is required as a minimum. | Agree |
| DE | 43 | 4.2.5 | 1st paragraph 1st dash | Technical |  | Please change: - the same nominal current rating or less; Add the following: - the same fuse time characteristic - the same fuse resistor value or higher | Agree |
| DE | 44 | 4.2.5 | 2nd paragraph | Technical | In case of issuing a certificate the assessment of an apparatus is restricted to an ExTL and ExCB. This clause gives the service facility the same responsibility as for ExTLs and ExCBs. This responsibility for the service facility is contents of several clauses in this standard and should be reconsidered. | Delete the second paragraph | Agree |
| NL | 45 | 4.2.5 | last paragraph | ###### Technical | NOT acceptable. In this case a new certificate is mandatory since it is a change to already certified equipment that certainly affects the intrinsic safety |  | Agree |
| DE | 46 | 4.2.6 |  | Technical | Relays as many other components can be selected or is in a special design, which is not recognizable by a service facility. | If a relay is faulty, it shall be replaced by one, which is identical obtained from the manufacturer of the apparatus. | “as agreed by the manufacturer” may be added. |
| DE | 47 | 4.2.8 | 2nd sentence | Technical | The content does not correspond to 60079-11 | Where varnish is damaged during repair, insulating varnish of the type prescribed by the manufacturer shall be applied in the approved Manner. e.g., one coat if using dipping, two coats using other methods. If the coating is applied by spraying, two separate coats shall be applied. Other methods of application require only one coat, for example dip coating, brushing, vacuum impregnating. | Agree |
| DE | 48 | 4.2.9 |  | Technical | In the most cases optocouplers cannot be replaced by an equivalent type because the most of the used optocouplers are measured to assess the relevant quality and the necessary protection is given by the apparatus. | Only components of the same or directly equivalent type and certification shall be used as replacements. | Agree |
| NL | 49 | 4.2.9 |  | Technical | only optocouplers with identical or higher ratings and with the same or larger creepage distances and clearances shall be used. “directly equivalent type” is not clear enough |  | Agree |
| DE | 50 | 4.2.10 |  | Technical | A manufacturer never accepts that such documentation is supplied with the equipment. It is also not in his interest to give such documents to a service facility (see also comment to clause 4). Further a service facility is not able to recognize these components. This is a further clause which leads to the decision to exclude type of protection “i” from this standard |  | See response to comment 36. |
| DE | 51 | 4.2.15 |  | Technical | The type of protection „i“ depends not on creepage and clearances distances only. This type of protection as well as all other type of protection depending on non-electrical parts also. Non-electrical parts can influence the creepage and clearances distances. | Where the apparatus has non-electrical parts, e.g., fittings or window, that do not affect the electrical circuit or creepage and clearance distances and hence the intrinsic safety, the influence of these parts on the type of protection has to be considered before may be replaced by new parts of equivalent type. | Agree |
| CN | 52 | 4.4 |  | Technical | In 3.4.1, 4.4, 5.4.1, 6.4.1 and 7.4.1 or in 2.6.3 add: It should, where appropriate, take account of the requirements of the apparatus standard to avoid frictional sparking and electrostatic charging add: It should, where appropriate, take account of the requirements of the apparatus standard to avoid frictional sparking and electrostatic charging |  | Agree |
| DE | 53 | 4.4 |  | Technical | How can a service facility decide whether or not a modification affect the intrinsic safety. | Exclude modifications. Delete paragraph 4 | Agree to revise. Should require reference to manufacturer and certifying authority for ALL modifications |
| NL | 54 | 5.2.6.3.2 |  | Technical | add the flux test here |  | Refer to WG10 |
| CN | 55 | 5.4.1 |  | Technical | In 3.4.1, 4.4, 5.4.1, 6.4.1 and 7.4.1 or in 2.6.3 add: It should, where appropriate, take account of the requirements of the apparatus standard to avoid frictional sparking and electrostatic charging add: It should, where appropriate, take account of the requirements of the apparatus standard to avoid frictional sparking and electrostatic charging |  | Agree |
| NL | 56 | 5.4.4 |  | Technical | NOT allowed, see comment to 3.4.4 |  | Refer to the response to comment 52. |
| NL | 57 | 6.2.6.1 |  | Technical | Not permitting copy-winding techniques is unacceptable. This technique is in use as long as Ex e exist without any problems. Unless there is strong evidence that this technique results in Ex e motors that are unsafe, copy-winding must be included in OD015 for Ex e motors, using the same requirements as for Ex n motors (see 7.2.6.1) |  | WG10 position has been not to permit this as it presents difficulties when the service facility does not know if the motor has previously been rewound |
| NL | 58 | 6.2.6.3.2 |  | Technical | add flux test here |  | Agree |
| CN | 59 | 6.4.1 |  | Technical | In 3.4.1, 4.4, 5.4.1, 6.4.1 and 7.4.1 or in 2.6.3 add: It should, where appropriate, take account of the requirements of the apparatus standard to avoid frictional sparking and electrostatic charging add: It should, where appropriate, take account of the requirements of the apparatus standard to avoid frictional sparking and electrostatic charging |  | Agree |
| NL | 60 | 6.4.1 |  | Technical | such modified apparatus must obtain a new certificate… |  | See response to comment 52 |
| NL | 61 | 6.4.4 |  | Technical | Rewinding NOT allowed, see comment to 3.4.4 |  | Agree |
| CN | 62 | 7 |  | Editorial | delete non-sparking |  | Noted |
| DE | 63 | 7.2.1 |  | Technical | Add a new paragraph which requires the assessment of the electrostatic discharge |  | Refer to WG10 |
| NL | 64 | 7.2.1 |  | Technical | please note that in Europe Ex n apparatus is usually not certified. Referring to the certification label gives therefore quite often problems, since there is no such label. Same problem in the last paragraph, where reference is made to the certification requirements |  | Refer to WG10 |
| NL | 65 | 7.2.6.3.2 |  | Technical | add flux test here |  | Agree |
| CN | 66 | 7.4.1 |  | Technical | In 3.4.1, 4.4, 5.4.1, 6.4.1 and 7.4.1 or in 2.6.3 add: It should, where appropriate, take account of the requirements of the apparatus standard to avoid frictional sparking and electrostatic charging add: It should, where appropriate, take account of the requirements of the apparatus standard to avoid frictional sparking and electrostatic charging |  | Agree |
| NL | 67 | 7.4.1 |  | Technical | see comment to 6.4.1 |  | See response to comment 52 |
| DE | 68 | 8 |  | ###### Technical | See comments to clause 4 |  | See response to comment 52 |
| NL | 69 | 8 |  | Technical | 2nd paragraph: must be deleted. Without certification documents one cannot obtain 100% certainty for compliance with the standards. Stating this has no use at all. |  | Refer to WG10 |
| CN | 70 | Annex C C1 and C2 |  | Technical | Comment: 1) In Clause C1 of Annex C, it is meant that safety of equipment repaired in compliance with relevant Ex standard is not reliable for use in potential explosive atmospheres. The equipment repaired or overhauled on base of primary joint set, e.g. construction and width, and in compliance with relevant standard can be used safely in potential explosive atmosphere, because the equipment Ex d have safety factor (for IIA,IIB 1.42,for IIC 1.85 as shown in IEC60079-1). In fact, safety factor is used in tests for non-transmission of an internal ignition in IEC60079-1, e.g. the gap IE may be 90% of the maximum constructional gap IC as specified in the manufacturer drawings. - 2)The values corresponding to 80% of the maximum allowable diametral gap given in Table C1 and the values corresponding to 40% of the maximum allowable gaps given in Table C2 are available in theory, but it is much difficult to achieve in praxis, because the tolerances in table are too small, particular for IIC in production 3)In this annex there is “If achievable, these reduced gaps may enable prolonging the use of equipment in injurious environments.” , but it is not indicated whether equipment repaired in compliance with standard can be used in potential explosive atmospheres. 4) Where the data in table C1 and C2 are from? | revise Annex C as informative or cancel it | Agree to revise as informative. Refer to WG10 |
| DE | 71 | A.1 |  | Technical | All repairs done must be comprehensible. If markings of earlier repairs are removed this has to be included in the records. | Please change the paragraph accordingly. | Refer to WG10 |
| NL | 72 | Annex A |  | Technical | Add A.2 to the heading “Symbols” |  | Noted |
| DE | 73 | Annex A | A.2.2 | Technical | This shall not be used for type of protection “i” | Add the following to the existing paragraph: This shall not be used for type of protection “i” | Refer to WG10 |
| NL | 74 | Annex A | A2.2 | Technical | delete A.2.2 |  | Refer to WG10 |