INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC)

IEC SCHEME FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES  (IECEx SCHEME)

IECEx OPERATIONAL DOCUMENT

No. Ex OD 015 Version 2

- Title: 	Additional Requirements for IECEx Service Facilities involved in repair, overhaul and modification of Ex equipment.

WG 10 PROPOSED NEW VERSION 2

- IECEx Operational Document

This Operational Document sets out requirements that supplement the general requirements of IEC 60079-19 and provides a common approach to the application and implementation of the 2nd Edition of IEC 60079-19.  This new Edition of OD 015 covers material additional to IEC 60079-19.

Use of this OD 015 is necessary in order for the IECEx Scheme to move forward and meet industry demands in providing a single global assessment and certification system for Ex Service Facilities.

This Draft Revised Version 2 of OD 015 has been prepared by WG10 arising from their 11 June 2007 Paris Meeting to take account of the new 2nd Edition IEC 60079-19 and is submitted for consideration by ExMC.

Comments from ExMC Members are requested to be submitted to the IECEx Secretariat no later than 20 August 2007.

Document History

| Date | Summary |
| --- | --- |
| 2006 07 | Original Issue (Version 1) |
| 2007 XX | Revision to take account of 2nd Edition IEC 60079-19 |

- INTRODUCTION

This IECEx Operational Document is for use by Service Facilities operating in the IECEx Service Facilities Scheme, as described in IECEx OD 013.  ExCBs may use the requirements of this document when evaluating Ex Service Facilities.

The procedures, systems and methods of repair as set out in this document are to be followed by Ex Service Facilities involved in the repair and overhaul of Ex equipment.

This Operational Document is to be read in conjunction with IEC 60079-19:2006, and is intended to cover items not covered by that standard.   Should any conflicts be observed then IEC 60079-19 is to be followed.  Specifications, detailed techniques, and industry practice are reflected in this document.

Compliance with this Operational Document will require Service Facilities to satisfy the requirements IEC 60079-19.

To assist with the understanding and use of this Operational Document, the Section and Clause numbering format of IEC 60079-19:2006 2nd Edition has been used, in order to clarify the both the stated and additional requirements  to the corresponding Clause of IEC 60079-19.

Therefore, it is imperative that this Operational Document be read in conjunction with IEC 60079-19:2006 2nd Edition.

CONTENTS

1	Scope	4

2	Normative references	4

3	Definitions and terms	4

4	General	4

5	Additional requirements: Protection “d” Flameproof	4

5.1	Tolerances of joints	4

5.2	Report Format Flameproof Motors	5

5.3	Machining limits for Flameproof surfaces	5

6	Additional requirements: Protection “I” Intrinsic Safety	5

7	Additional requirements: Protection “p” Pressurized	5

8	Additional requirements: Protection “e” Increased Safety	5

9	Additional requirements: Protection “n” Non sparking	5

10	Additional requirements: Standard IEC 60079-26	5

11	Additional requirements: Protection “tD”	6

12	Additional requirements: Protection “pD” Pressurized	6

IEC 60079-19 Annex A: Identification of repaired equipment by marking	6

IEC 60079-19 Annex B: Knowledge, skills and competencies of “Responsible Persons” and “Operatives”	6

IEC 60079-19 Annex C: Requirements for measurements in flameproof equipment	6

Annex A RECOMMENDED REPORT FORMS	7

A.1	Report for motors - protection type “d” (flameproof)	8

A.2	Report for enclosures - protection type “d” (flameproof)	10

A.3	Report for equipment installed within enclosures - protection type ‘d’	12

A.4	Report for equipment - protection type “i” (intrinsic safety)	15

A.5	Report for enclosures and transformers - protection type “p”	16

A.6	Report for motors – protection type “e” (increased safety)	17

A.7	Report for enclosures – protection type “e” (increased safety)	19

A.8	Report for equipment within enclosures – protection type “e”	20

A.9	Report for motors – protection type “n” (non-sparking)	21

A.10	Report for enclosures – protection type “n” (non-sparking)	23

A.11	Report for motors – protection type “tD”	24

A.12	Report for enclosures – protection type “tD”	26

A.13	Report for equipment inside enclosures – protection type “tD”	27

A.14	Assessment of Responsible Persons and Operatives	41

Annex B ADDITIONAL INFORMATION	42

B.1	OVER-PRESSURE TEST PROCEDURE	42

B.1.1	INTRODUCTION	42

B.1.2	TEST PROCEDURE	42

B.1.3	REPORTING OF RESULTS	42

B.1.4	INTERPRETATION OF RESULTS	43

B.2	MACHINING LIMITS	44

- INTERNATIONAL ELECTROTECHNICAL COMMISSION

# Scope

There are no additional requirements to those of IEC 60079-19.

# Normative references

There are no additional requirements to those of IEC 60079-19.

# Definitions and terms

There are no additional requirements to those of IEC 60079-19.

NOTE: Definitions covering IECEx Certified Service Program exist in IECEx 03, OD 013, OD 014

# General

Where the Service Facility has doubt or questions the validity of documentation or where no or insufficient documentation exists, the following tests shall be conducted

- For flameproof protection type “d” enclosures - an overpressure test in accordance with Annex B.1 to the following:

The pressure to be used for the over-pressure test should be either the value mentioned in the certification documents for such purpose or 1.5 times the reference pressure.

If neither the over-pressure test value or the reference pressure test value are known, the values for the pressure test should be:

- For Group I, Group II A and B - 1050 kPa. / (10.5 bar)

- For Group II C - 1500 kPa. (15 bar)

- For dust ignition protection type ”tD” or similar enclosures, an IP test in accordance with IEC 60529.  The IP rating to be met shall comply with IEC 61241-1.

The requirements of this document apply where IEC 60079-19 does not completely specify the method of repair, overhaul or test for a particular Ex technique.

# Additional requirements: Protection “d” Flameproof

For IECEx Service Facility Scheme, the requirements of IEC 60079-19 apply, plus the following.

## Tolerances of joints

The following notes may be read in conjunction with Clause 8.2 of IEC 60079-1 fourth edition and may also be applied in principle for earlier editions:

NOTE 1: It is acknowledged that, with assemblies, all parts will not exist at the worst-case dimensions simultaneously.  A statistical treatment of the tolerances, such as “RMS”, may be required for m and k verification.

NOTE 2: It is not a requirement of this standard that the manufacturer’s m and k calculations be verified.  Also, it is not a requirement of this standard that m and k be verified by measurement

Threaded holes relevant to the protection concept are verified by use of “Go-NoGo” gauges

## Report Format Flameproof Motors

At the completion of the repair or overhaul the Service Facility shall provide a report in such a format that aligns with the following examples:

- a) Sample Report format – Flameproof Motors, see Annex A.1,A.2,A3,A.4,A.5

- b) Sample Report Format – Flameproof Enclosures, see Annex A.24,A.5,

- c) Sample Report Format – Equipment within Flameproof Enclosures, see Annex A.3.

## Machining limits for Flameproof surfaces

The additional information in B.2 of this document provides general limits for machining.

# Additional requirements: Protection “I” Intrinsic Safety

For IECEx Service Facility Scheme, the requirements of IEC 60079-19 apply, plus the following.

Ex i equipment shall only be repaired or overhauled where an agreement exists between the manufacturer and service facility.

At the completion of the repair or overhaul the Service Facility shall provide a report in such a format that aligns with the following example:

Sample Report format – Intrinsic Safety, see A.5.

# Additional requirements: Protection “p” Pressurized

For IECEx Service Facility Scheme, the requirements of IEC 60079-19 apply, plus the following.

At the completion of the repair or overhaul the Service Facility shall provide a report in such a format that aligns with the following example:

Sample Report format – Pressurized Enclosures and Transformers see A.6 .

# Additional requirements: Protection “e” Increased Safety

For IECEx Service Facility Scheme, the requirements of IEC 60079-19 apply, plus the following.

At the completion of the repair or overhaul the Service Facility shall provide a report in such a format that aligns with the following examples:

- a) Sample Report format – Increased Safety Motors - see A.7

- b) Sample Report format – Increased Safety Enclosures - see .

- c) Sample Report format – Equipment within Increased Enclosures - see A.8.

# Additional requirements: Protection “n” Non sparking

For IECEx Service Facility Scheme, the requirements of IEC 60079-19 apply, plus the following.

At the completion of the repair or overhaul the Service Facility shall provide a report in such a format that aligns with the following examples:

- Sample Report format – Non Sparking Motors, see A.9

- Sample Report format – Non Sparking Enclosures, see A.10

# Additional requirements: Standard IEC 60079-26

There are no additional requirements to those of IEC  60079-19.

# Additional requirements: Protection “tD”

For IECEx Service Facility Scheme, the requirements of IEC 60079-19 apply, plus the following.

At the completion of the repair or overhaul the Service Facility shall provide a report in such a format that aligns with the following examples:

- a) Sample Report format – Protection type “tD” Motors, see A.11

- b) Sample Report Format – Protection type “tD” Enclosures, see A.12

- c) Sample Report Format – Equipment within type “tD” Enclosures, see A.13

# Additional requirements: Protection “pD” Pressurized

There are no additional requirements to those of IEC 60079-19.

# IEC 60079-19 Annex A: Identification of repaired equipment by marking

There are no additional requirements to those contained in IEC 60079-19.

# IEC 60079-19 Annex B: Knowledge, skills and competencies of “Responsible Persons” and “Operatives”

For IECEx Service Facility Scheme, the requirements of IEC 60079-19 apply, plus the following apply.

Every Service Facility site shall have a minimum of one Responsible Person in the area of explosion-protection listed in the Service Facility Scope. That person shall be directly associated with and responsible for the assessment of the relevant explosion-protected electrical equipment.

Verification of knowledge, skills and competencies of Responsible Persons and Operatives shall include

- A working knowledge of the relevant Ex Standard by those making decisions to the status of Ex equipment

- Review of qualifications and work history relevant to IEC 60079-19 requirements,

- Technical interview about explosive atmospheres and zones, gas groups and explosion protection techniques,

- Witnessing of work done, use of tools and test equipment, understanding of calibration and measurement traceability.

NOTE:

- List of suggested questions is given in Annex A.17

- Any training and assessment of competencies should cover the above as a minimum.

- IECEx WG12 is currently developing competency requirements in this arera.

# IEC 60079-19 Annex C: Requirements for measurements in flameproof equipment

There are no additional requirements to those of IEC 60079-19.

- RECOMMENDED REPORT FORMS

- Informative

This Annex contains a collection of Standardised Report forms that may be used by Service Facilities involved in the repair, overhaul or modification of Ex equipment.

While Service Facilities are free to use their own report formats, those used by the Service Facility should contain the same level of information as that detailed in these sample forms.

ExCBs shall use this Annex as a guide when determining the suitability of such forms used by Service Facilities in the IECEx Service Facility Scheme.

  - Report for motors - protection type “d” (flameproof)

| Report no.: Certificate no.: Name of Service Facility Service facility recognition no.: Location: Country: Motor description: Serial no.: Owner: Order no.: Date received: | Flameproof Motors: Shaft flameproof Gland diametral clearance—D.E.: mm N.D.E.: mm Endplate spigot diametral clearance—D.E.: mm N.D.E.: mm Cable gland and gland spigot diametral clearance: mm Screwed cable gland no. of threads engaged: Screwed hand hole covers no. of threads engaged Condition of bolt holes: Terminal box: Deviation of flanged joint surfaces (max): mm Flamepath gap after assembly: mm Water jacket: Jacket volume test before descaling: litres Jacket thickness: mm Jacket pressure test: kPa at: °C Pass: Fail: Jacket descaled by using: Volume test after descaling: litres Flow test: litres/min Static pressure test: Terminal boxes: kPa Motor enclosures: kPa Tests: Insulation test to frame: Volt megger Stator/fields: Rotor/Armature: Test run for 1 hour—phase Currents— A: B: C: Core test—stator: Rotor: Previous core test—Stator: Rotor: |  |
| --- | --- | --- |
| Motor condition when dismantled: Drive End (D.E); Non Drive End (N.D.E) Bearings and seals—D.E.: N.D.E: Bearing journals—D.E.: N.D.E Seals journals —D.E.: N.D.E: Bearings housings—D.E.: N.D.E. Stator and windings: Rotor/armature and windings: Items missing on receipt of motor: General motor condition: Details of motor repair: Bearing make and no.:—D.E.: N.D.E.: Seal make and no.—D.E.: N.D.E.: Replacement shaft manufacturer: |  |  |
| Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES / NO / NA Mark which applies to released product. |  |  |
| Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . . |  |  |

- FLAME DEFLECTOR INSPECTION FOR Exd  MOTORS

|  | Good |  | Meas. by | Must rep | Meas. by |  | Rep | Done by |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| #### Bearing shield |  |  |  |  |  |  |  |  |
| Bearing fit DE1 |  |  |  |  |  |  |  |  |
| Bearing fit ND2 |  |  |  |  |  |  |  |  |
| #### AXLE |  |  |  |  |  |  |  |  |
| Bearing seat DE 3 |  |  |  |  |  |  |  |  |
| Bearing seat ND 4 |  |  |  |  |  |  |  |  |
| #### Cast |  |  |  |  |  |  |  |  |
| Axle key DE 5 |  |  |  |  |  |  |  |  |
| Axle key ND 6 |  |  |  |  |  |  |  |  |
| Fan position/- |  |  |  |  |  |  |  |  |
| Fan |  |  |  |  |  |  |  |  |
| Crack test, axle |  |  |  |  |  |  |  |  |
| Seal pos DE |  |  |  |  |  |  |  |  |
| Seal pos ND |  |  |  |  |  |  |  |  |
| HUB position on axle. |  | Before |  |  | Now |  |  |  |

  - Report for enclosures - protection type “d” (flameproof)

| Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no.:. Fax no.: Enclosure description: Serial no.: Owner: Order no.: Date received: . . . ./. . . ./. . . . |  |  |
| --- | --- | --- |
| Item | Description of check | Remarks |
| (a) | Check of external and internal damage |  |
| (b) | Dimensional check |  |
| (c) | Corrosion on flamepaths |  |
| (d) | Result of static pressure test |  |
| (e) | Check of flanged joint surfaces |  |
| (f) | Check of all threaded holes |  |
| (g) | Check of all windows and lenses |  |
| (h) | Check of breathers |  |
| (i) | Check of all bolt holes, studs, screws, etc. |  |
| (j) | Check of all gland entries and fixing holes |  |
| (k) | Check of all cables glands |  |
| (l) | Check of all handhole and inspection covers |  |
| (m) | Check of all mechanical interlocks |  |
| (n) | Check of all flamepath gaps |  |
| Main control panel 1 Max. out of plane of box flanges: 2 Max. out of plane of cover: 3 Max. flameproof gap when bolted up: 4 Max. diametral clearance of spindles: 5 Max. diametral clearance of gland to gland apertures: 6 Static pressure test—pressure: 7 Water jacket—pressure test: Capacity: |  |  |
| Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES/NO/NA Mark which applies to released product. |  |  |
| Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . . |  |  |

- FLAME DEFLECTOR INSPECTION FOR Exd Flameproof Enclosures

All measurements in 1/1000 mm.

| TERMINAL BOX | Good | Meas. by | Must rep | Meas. by | Rep | Done by |
| --- | --- | --- | --- | --- | --- | --- |
| Flame deflector 11a |  |  |  |  |  |  |
| Flame deflector 11b |  |  |  |  |  |  |
| Flame deflector 12a |  |  |  |  |  |  |
| Flame deflector 12b |  |  |  |  |  |  |
| Flame deflector 13a |  |  |  |  |  |  |
| Flame deflector 13b |  |  |  |  |  |  |
| Flame deflector 14a |  |  |  |  |  |  |
| Flame deflector 14b |  |  |  |  |  |  |
| Screw hole | Dim |  | Dim |  |  |  |

- See also B2 for limits

  - Report for equipment installed within enclosures - protection type ‘d’

| Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no.: Fax no.: Description of unit: Owner: Order no.: Serial no of enclosure this test certificate applies to.: Enclosure test certificate no.: Date received: . ./. . . ./. . . . |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Description of check |  | No work required |  | Overhauled |  | Repaired | Replaced (R) Modified (M) |  |
| (a) | Isolator mechanism and switch operation |  |  |  |  |  |  |  |  |
| (b) | Earthing device and operation |  |  |  |  |  |  |  |  |
| (c) | All auxiliary mechanisms, trip bars, latching arrangements, etc. |  |  |  |  |  |  |  |  |
| (d) | All locking devices, function and operation |  |  |  |  |  |  |  |  |
| (e) | All parts for mechanical condition |  |  |  |  |  |  |  |  |
| (f) | All insulation checked—no heat, cracks, etc. |  |  |  |  |  |  |  |  |
| (g) | Phase barriers fitted correctly and functional |  |  |  |  |  |  |  |  |
| (h) | Oil levels and/or gas pressure |  |  |  |  |  |  |  |  |
| (i) | Gas pressure-sensing devices |  |  |  |  |  |  |  |  |
| (j) | All wiring and terminations |  |  |  |  |  |  |  |  |
| (k) | Earth continuity; phase/earth fault lock units |  |  |  |  |  |  |  |  |
| (l) | Overcurrent, overload and earth-fault devices |  |  |  |  |  |  |  |  |
| (m) | Earth-fault trip devices |  |  |  |  |  |  |  |  |
| (n) | Timing devices |  |  |  |  |  |  |  |  |
| (o) | Temperature-sensing devices |  |  |  |  |  |  |  |  |
| (p) | Transformer connections, bolts, tapes, bracing, insulators and fittings etc. |  |  |  |  |  |  |  |  |
| (q) | Installation |  |  |  |  |  |  |  |  |
| (r) | Machine cables and glands |  |  |  |  |  |  |  |  |
| Details of overhaul, repair or modification (attach extra pages if required): |  |  |  |  |  |  |  |  |  |
| Results of insulation resistance tests on transformers: Transformer ratio: Capacity: Serial no: Manufacturer: Type of cooling: Tested with: V (megohmmeter) Primary winding to secondary winding: MΩ Primary winding to earth: MΩ Secondary winding to earth: MΩ Earth continuity of earth screen to core: Assembled unit tested for insulation resistance with: V megohmmeter, and power frequency tested on the following circuits: |  |  |  |  |  |  |  |  |  |
| Circuit description |  | Insulation resistance |  | Test voltage |  | Test frequency |  |  | Result |
|  |  | MΩ |  | kV |  | Hz |  |  |  |
| Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES/ NO /NA Mark which applies to released product. |  |  |  |  |  |  |  |  |  |
| Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . . |  |  |  |  |  |  |  |  |  |

  - This Paragraph indicates the checks to be performed on circular flanges, spigots and holes using inside and outside micrometers and dial gauges. These checks shall be carried out in accordance with the figures below.

Diametral Check

Flange Flatness and Spigot Depth Check

End Cover Flatness Diametral and Spigot Depth Check

  - Report for equipment - protection type “i” (intrinsic safety)

Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no.: Fax no.: Equipment description: Owner: Order no.: Serial no.: Date received: . . . ./. . . ./. . . .

Reference to User Works/Contract Instructions:………………………………………………..

Condition upon receipt: Old repair label details: Cert no.:

Reported fault (if any):

Repair action:

Parts replaced:

Tests performed:

Results:

Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES / NO / NA Mark which applies to released product.

Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . .

  - Report for enclosures and transformers - protection type “p”

Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no.: Fax no.: Equipment description: Owner: Order no.: Serial no: Date received: . . . ./. . . ./. . . .

Condition upon receipt: Old repair label details: Cert no.:

Reported fault (if any):

Repair action: Parts replaced:

Test performed: Results:

Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES / NO / NA Mark which applies to released product.

Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . .

  - Report for motors – protection type “e” (increased safety)

Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no: Fax no.: Motor description: Owner: Order no.: Serial no: Date received: . . . ./. . . ./. . . .

Motor condition when received: Old repair label no.: External surfaces cleaned for inspection— Fan cowls and fans: Stator case and cooling fins: Corrosion: Endshields and fasteners: Bearing caps: Ducts and piping: Grease relief: Terminal box cover and gaskets: Gland entries: Glands: General external condition: Missing parts: Motor dismantled: Degree of protection: IP Internal condition—Evidence of dust or liquids: Drive End D.E; Non Drive End N.D.E Bearings and seal— D.E.: Bearing journals— D.E.: N.D.E.: NDE.: Seals journals— D.E.: Bearing housings— D.E.: N.D.E.: N.D.E.: Stator windings and iron circuit: Rotor cage and iron circuit: Internal fan clearance: Details of motor repair:

Ex ‘e’ motor Cover and fasteners: Condition of fastener holes: Gasket: Gland entries: Terminals type: Certificate no.: Cable lugs type: Sleeving fitted Stator—Dia: Winding to original certification: or modified: Rotor—Dia: Radial gap: Minimal Radial Gap according IEC 60079-7:……………………………..... Replaced—Radial gap: Overload type: Tests: Resistance cold (ohms)—Amb. Temp C Phases— A B C Core test —Previous stator: Rotor: —Present stator: Rotor: Insulation test to frame: Phase/Phase: A B D H.V. test to IEC 60079-7 kV for 1 minute. No load running—Vibration: Noise: Bearing heat: Phase balance—Reduced voltage: A B C (at full load amps) (Locked rotor) OR Rated full load: A B C Temperature increase test—Full load: K Temperature class: T Locked rotor: IA / IN tE secs.

Certification drawing no(s).: Remarks: Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES / NO / NA Mark which applies to released product.

Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . .

- Report for enclosures – protection type “e” (increased safety)

Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no: Fax no.: Enclosure description: Owner: Order no.: Serial no: Date received: . . . ./. . . ./. . . .

Enclosure condition when received: Old repair label no.: External surfaces cleaned for inspection— Covers and fasteners: Base of enclosure: Threaded holes: External corrosion: Surface coating: Gland entries and glands: General external condition: Enclosure dismantled: Degree of protection: IP Internal condition—Dust: Corrosion: or, evidence of liquids: Heat: Missing parts: Cables and terminations: Terminal blocks: Earth terminals: General insulation: Windows and seals: Actuators and seals: Ex ‘de’ parts: Meters: Lamps: Transformers: Switches: Other: Relays: Interlocks: Luminaire: Lamp type and power (W): Transparent part: Lampholders: Ballasts: Capacitors: Batteries:

Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES / NO / NA Mark which applies to released product

Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . .

  - Report for equipment within enclosures – protection type “e”

| Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no: Fax no.: Description of unit: Owner: Order no.: Serial no of enclosure this test certificate applies to: Enclosure test certificate no.: Date received: . . . ./. . . ./. . . . |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Description of work | No work required | Overhauled | Repaired | Replaced (R) Modified (M) |
| (a) | Ex ‘e’ lamp |  |  |  |  |
| (b) | Ex ‘e’ switch |  |  |  |  |
| (c) | Ex ‘e’ meter—calibrate |  |  |  |  |
| (d) | Switch actuator—check all seals and action |  |  |  |  |
| (e) | Terminal blocks—check for heat and insulation cracks + Certification details |  |  |  |  |
| (f) | Bushings and insulation condition |  |  |  |  |
| (g) | Cables—insulation, lugs and sleeving |  |  |  |  |
| (h) | Transformer connections, tapes, bracing insulators, terminal |  |  |  |  |
| (i) | Temperature sensing devices |  |  |  |  |
| (j) | Mechanical interlocks |  |  |  |  |
| (k) | All insulation checked—no heat |  |  |  |  |
| (l) | Heaters—check condition |  |  |  |  |
| Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES / NO / NA Mark which applies to released product |  |  |  |  |  |
| Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . . |  |  |  |  |  |

  - Report for motors – protection type “n” (non-sparking)

Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no.: Fax no.: Motor description: Owner: Order no.: Serial no: Date received: . . . ./. . . ./. . . .

Motor condition when received: Old repair label no.: External surfaces cleaned for inspection— Fan cowls and fans: Stator case and cooling fins: Corrosion: Endshields and fasteners: Bearing caps: Ducts and piping: Grease relief: Terminal box cover and gaskets: Gland entries: Glands: General external condition: Missing parts: Motor dismantled: Degree of protection: IP Internal condition—Dust: or, evidence of liquids: Drive End D.E; Non Drive End N.D.E Bearings and seal— D.E.: Bearing journals— D.E.: N.D.E.: NDE.: Seals journals— D.E.: Bearing housings— D.E.: N.D.E.: N.D.E.: Stator windings and iron circuit: Rotor cage and iron circuit: Internal fan clearance:

Details of motor repair: Ex ‘n’ motor Cover and fasteners: Condition of fastener holes: Gasket: Gland entries: Terminals type: Certificate no.: Cable lugs type: Sleeving fitted: Stator—Dia: Winding to original certification: or modified: Rotor—Dia: Radial gap: Minimum Radial Gap according to IEC 60079-15:……………………………..... Replaced—Radial gap: Overload type: Tests: Resistance cold (ohms)—Amb. Temp C Phases— A B C Core test —Previous stator: Rotor: —Present stator: Rotor: Insulation test to frame: Phase/Phase: A B D H.V. test to IEC 60079-15: kV for 1 minute. No load running—Vibration: Noise: Bearing heat: Phase balance—Reduced voltage: A B C (at full load amps) (Locked rotor) OR Rated full load: A B C Temperature increase test—Full load: K Temperature class: T

Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES / NO / NA Mark which applies to released product

Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . .

  - Report for enclosures – protection type “n” (non-sparking)

Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no.: Fax no.: Enclosure description: Owner: Order no.: Serial no: Date received: . . . ./. . . ./. . . .

Enclosure condition when received: Old repair label no.: External surfaces cleaned for inspection— Covers and fasteners: Base of enclosure: Threaded holes: External corrosion: Surface coating: Gland entries and glands: General external condition: Enclosure dismantled: Degree of protection: IP Internal condition—Dust:: Corrosion: or, evidence of liquids: Heat: Missing parts: Cables and terminations: Terminal blocks: Earth terminals: General insulation: Windows and seals: Actuators and seals: Ex ‘n’ parts: Meters: Lamps: Transformers: Switches: Other: Relays: Interlocks: Luminaire: Lamp type and power (W): Transparent part: Lampholders: Ballasts: Capacitors: Batteries: Enclosure assembled: Restricted breathing test: Type of test:

Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES / NO / NA Mark which applies to released product.

Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . .

  - Report for motors – protection type “tD”

Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no.: Fax no.: Motor description: Owner: Order no.: Serial no: Date received: . . . ./. . . ./. . . .

Motor condition when received: Old repair label no.: External surfaces cleaned for inspection— Fan cowls and fans: Stator case and cooling fins: Corrosion: Endshields and fasteners: Bearing caps: Ducts and piping: Grease relief: Terminal box cover and gaskets: Gland entries: Glands: General external condition: Missing parts: Motor dismantled: Degree of protection: IP Internal condition—Evidence of dust or liquids: Drive End D.E; Non Drive End N.D.E Bearings and seal— D.E.: Bearing journals— D.E.: N.D.E.: NDE.: Seals journals— D.E.: Bearing housings— D.E.: N.D.E.: N.D.E.: Stator windings and iron circuit: Rotor cage and iron circuit: Internal fan clearance: Details of motor repair:

- Protection type ‘tD’ motor with Ex ‘tD’ terminal box: (Refer to Certificate for ‘tD’): [Protection ‘tD’ was formerly known as DIP.] Cover and fasteners: Condition of fastener holes: Gasket: Gland entries: Terminals type: Certificate no.: Cable lugs type: Sleeving fitted: 2. DIP Motor – Item 1 plus: Stator—Dia: Winding to original approval: or Modified: Rotor—Dia: Radial gap: Replaced—Radial gap: Overload type: Tests: Resistance cold (ohms)—Amb. Temp C Phases— A B C Core test —Previous stator: Rotor: —Present stator: Rotor: Insulation test to frame: Phase/Phase: A B D H.V. test kV for 1 minute. No load running—Vibration: Noise: Bearing heat: Phase balance—Reduced voltage: A B C (at full load amps) (Locked rotor) OR Rated full load: A B C Temperature increase test—Full load: K Temperature class: T

Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES / NO / NA Mark which applies to released product.

Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . .

  - Report for enclosures – protection type “tD”

Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no: Fax no.: Enclosure description: Owner: Order no.: Serial no: Date received: . . . ./. . . ./. . . .

Enclosure condition when received: Old repair label no.: External surfaces cleaned for inspection— Covers and fasteners: Base of enclosure: Threaded holes: External corrosion: Surface coating: Gland entries and glands: General external condition: Enclosure dismantled: Degree of protection: IP Internal condition—Dust: Corrosion: or, evidence of liquids: Heat: Missing parts: Cables and terminations: Terminal blocks: Earth terminals: General insulation: Windows and seals: Actuators and seals: DIP parts: Meters: Lamps: Transformers: Switches: Other: Relays: Interlocks: Luminaire: Lamp type and power (W): Transparent part: Lampholders: Ballasts: Capacitors: Batteries:

Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES / NO / NA Mark which applies to released product.

Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . .

  - Report for equipment inside enclosures – protection type “tD”

| Report no.: Certificate no.: Name of overhaul service facility: Service facility recognition no.: Address: Postcode: Telephone no.: Fax no.: Description of unit: Owner: Order no.: Serial no of enclosure this test certificate applies to: Enclosure test certificate no.: Date received: . . . ./. . . ./. . . . |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Description of work | No work required | Overhauled | Repaired | Replaced (R) Modified (M) |
| (a) | Lamp |  |  |  |  |
| (b) | Switch |  |  |  |  |
| (c) | Meter—calibrate |  |  |  |  |
| (d) | Switch actuator—check all seals and action |  |  |  |  |
| (e) | Terminal blocks—check for heat and insulation cracks |  |  |  |  |
| (f) | Bushings and insulation condition |  |  |  |  |
| (g) | Cables—insulation, lugs and sleeving |  |  |  |  |
| (h) | Transformer connections, tapes, bracing insulators, terminal |  |  |  |  |
| (i) | Temperature sensing devices |  |  |  |  |
| (j) | Mechanical interlocks |  |  |  |  |
| (k) | All insulation checked—no heat |  |  |  |  |
| (l) | Heaters—check condition |  |  |  |  |
| Certification drawing no(s).: Certification marking: I, confirm that the above equipment, has been repaired and repaired/overhauled in accordance with IEC 60079-19. The marking complies with Annex A of the standard. Summary of identification of released product a) Product conforms to original standard and certification documents YES / NO b) Restrictions apply to use of this product as originally certified YES / NO c) Compliance of the product has been verified by a competent person YES / NO / NA Mark which applies to released product. |  |  |  |  |  |
| Name of Responsible Person Signature Service Facility Record number.: Date: . . ./ . . ./ . . |  |  |  |  |  |

  - COMMON WORK REPORT Ex AC – MOTORS

- DESCRIPTION OF WORK TASK, TECHNICAL DATA, AND DESCRIPTION OF MOTOR DATA

| Motor manufacturer |  |
| --- | --- |
| Type |  |
| Motor No. |  |
| Ex classification |  |
| Classification number |  |
| Temperature class |  |
| Ia/In |  |
| Te time |  |
| Power [kW] |  |
| Voltage [V] |  |
| Current [A] |  |
| Cos phi |  |
| Frequency [Hz] |  |
| RPM [/min] |  |
| Coupling |  |
| Duty |  |
| IP degree |  |
| Weight |  |
| Insulation class |  |
| App. volume |  |

- EQUIPMENT

| EQUIPMENT | YES/NO | EQUIPMENT | YES/NO |
| --- | --- | --- | --- |
| Axle shaft key |  | Fan cover |  |
| Double axle |  | Base |  |
| Coupling/disc |  | Offshore HUB |  |
| Flange/upper guide edge |  | Gear rim |  |
| Feet |  | Eye bolt |  |
| Cable |  | Heating element |  |
| Plug |  | Thermistors |  |
| Com dismantled |  | Nipple plate |  |
| Coupling housing |  | Junction box, right |  |
| Fan |  | Junction box top |  |
|  |  | Junction box left |  |

- RECEIPT OF GOODS REPORT

| Customer |  |
| --- | --- |
| Address |  |
| Destination |  |
| Tag No. |  |
| Order No. |  |
| Our Order No. |  |
| Marks |  |
| Contact person |  |
| Previous Order No. |  |
| Person responsible |  |
| Installing engineer/mechanic |  |
| Estimated delivery date |  |
| Max time to condition report |  |
| RECERTIFICATION No. |  |

- MEASURING RESULT

| 500 V Pos earth |  |  | 500 V Neg earth |  |  |
| --- | --- | --- | --- | --- | --- |
| Stator/earth |  |  |  |  |  |
| Rotor/earth |  |  |  |  |  |
| Heating element | Value |  | Ohm |  | Mohm |
| Sensors | Value |  | Ohm |  | Mohm |
| Other | Value |  | Ohm |  | Mohm |

Baker test: 	Passed 	Failed

| Date: |  | Done by: |  |
| --- | --- | --- | --- |

- STATISTICAL MATERIAL

The objective of this material is to provide the customer with an improved overview of the electrical motor’s future secure operating period.

Measurements on arrival:

Measurement type:  Make   Measured on rig   Epoxy   Other

| Surface inspection | Good condition | Partially rusted | High level of rust | Destroyed by rust |
| --- | --- | --- | --- | --- |
| Covers/ housings |  |  |  |  |
| Motor housing |  |  |  |  |
| Signs/plates |  |  |  |  |
| Internal |  |  |  |  |

| Winding inspection | Impregnation good | Average | Poor | Salt |
| --- | --- | --- | --- | --- |
| Stator winding |  |  |  |  |
| Rotor winding |  |  |  |  |

| Bearing inspection | No special faults | Wear damage | Defect |
| --- | --- | --- | --- |
| Drive side |  |  |  |
| None drive side |  |  |  |

| Flame deflectors | Rust | Dry | Lubricated |
| --- | --- | --- | --- |

| Date: |  | Done by: |  |
| --- | --- | --- | --- |

- BEARING POSITION REPORT

|  | Good |  | Meas. by | Must rep | Meas. by |  | Rep | Done by |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Bearing shield |  |  |  |  |  |  |  |  |
| Bearing fit DE1 |  |  |  |  |  |  |  |  |
| Bearing fit ND2 |  |  |  |  |  |  |  |  |
| AXLE |  |  |  |  |  |  |  |  |
| Bearing seat DE 3 |  |  |  |  |  |  |  |  |
| Bearing seat ND 4 |  |  |  |  |  |  |  |  |
| Cast |  |  |  |  |  |  |  |  |
| Axle key DE 5 |  |  |  |  |  |  |  |  |
| Axle key ND 6 |  |  |  |  |  |  |  |  |
| Fan position/- |  |  |  |  |  |  |  |  |
| Fan |  |  |  |  |  |  |  |  |
| Crack test, axle |  |  |  |  |  |  |  |  |
| Seal pos DE |  |  |  |  |  |  |  |  |
| Seal pos ND |  |  |  |  |  |  |  |  |
| HUB position on axle. |  | Before |  |  | Now |  |  |  |

Junction box seen from AS Right    Left      Top  Feed-throughs:

|  | Good | Must rep. | Done date | Done by |
| --- | --- | --- | --- | --- |
| Inspected |  |  |  |  |
| Threads |  |  |  |  |

- WORK REPORT Ex AC Motors

|  | Date | Done by |
| --- | --- | --- |
| Sandblasted/Zink coated motor |  |  |
| Marked phase sequence |  |  |
| Disass. Motor w/condition inspection |  |  |
| Inspected feed throughs to terminal box |  |  |
| Inspected and ordered new plates as necessary |  |  |
| Washed stator with high pressure hot water and soap |  |  |
| Washed rotor with high pressure hot water and soap |  |  |
| Stator cleaned in tray hours |  |  |
| Rotor cleaned in tray hours |  |  |
| Dried rotor and stator until insulation curve flattened out at max value No. of hours |  |  |
| Mohm rotor at  C |  |  |
| Mohm stator at  C |  |  |
| Repaired flame deflectors |  |  |
| Wound stator winding |  |  |
| Impregnation |  |  |
| Vacuum pressure impregnation - stator |  |  |
| Vacuum pressure impregnation - rotor |  |  |
| Renewed seal DE ND |  |  |
| Inspection nipples |  |  |
| Inspection foot screws/earth point |  |  |
| Refurbishment glassblower parts |  |  |
| Mechanical repairs/ turning slip rings |  |  |
| Balancing of rotor |  |  |
| Installation of motor with new bearings |  |  |
| Lacquered motor |  |  |
| Recertification No. |  |  |
| Other |  |  |

- BALANCING DATA

All measurements in mm 	Weights in grams.

| A = |  | B = |  | C = |  |
| --- | --- | --- | --- | --- | --- |
| R1 = |  | R2 = |  | Key weight |  |

Dynamic imbalances on start:

| Position 1 |  | Gram | At |  | Degrees |
| --- | --- | --- | --- | --- | --- |
| Position 2 |  | Gram | At |  | Degrees |

Remaining imbalances after balancing:

| Position 1 |  | Gram | At |  | Degrees |
| --- | --- | --- | --- | --- | --- |
| Position 2 |  | Gram | At |  | Degrees |

| Date: |  | Done by: |  |
| --- | --- | --- | --- |

  - TEST RUN FORM FOR EX- MOTORS

- MEASURED VALUES:

| Instrument |  | Calibrated |  |
| --- | --- | --- | --- |
| Voltage |  | Frequency |  |
| Power |  | Current |  |
| /min |  |  |  |

Motor Top test 	Passed  		Failed

- TEMPERATURE MEASUREMENTS

Motor temperature class

| Instrument |  | Calibrated |  |
| --- | --- | --- | --- |
| Time | Bearing position DE | Stator | Bearing position ND |
| T. |  |  |  |
| T. |  |  |  |
| T. |  |  |  |
| T. |  |  |  |
| T. |  |  |  |
| T. |  |  |  |
| T. |  |  |  |
| T. |  |  |  |

Maximum temperature (T. Class inspection)

Temperature Cl. -40C + room temperature:     -40 +      =

Highest temperature achieved:

| Date: |  | Done by: |  |
| --- | --- | --- | --- |

  - FINAL INSPECTION

| FIELD WINDING |  |  |  | ANCHOR WINDING |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Instrument |  | Calibrated |  |  | Instrument |  | Calibrated |  |

| Insulation measurement |  | Mohm | Insulation measurement |  | Mohm |
| --- | --- | --- | --- | --- | --- |
| Calibration voltage |  | Volt | Calibration voltage |  | Volt |
| Temperature |  | C | Temperature |  | C |

| Instrument |  |  | Calibrated |  |  |
| --- | --- | --- | --- | --- | --- |
| Ohmic value sensors |  |  |  | Ohm |  |
| Ohmic value heating element |  |  |  | Ohm |  |
| Insulation measurement heating element |  |  |  | Mohm |  |

| Date: |  | Done by: |  |
| --- | --- | --- | --- |

- BEARING ANALYSIS

| Instrument |  |  |  | Calibrated |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Bearing drive side |  | Dismounted |  |  | Installed |  |  |
| Bearing measurement |  | Passed |  |  | Failed inspection |  |  |
| Bearing fan side |  | Dismounted |  |  | Installed |  |  |
| Bearing measurement |  | Passed |  |  | Failed inspection |  |  |

| Date: |  | Done by: |  |
| --- | --- | --- | --- |

BEARING GREASE TYPE :

| Date: |  | Done by: |  |
| --- | --- | --- | --- |

ANGLE OF ANGLE CONTACT BEARING

- SURFACE TREATMENT SPECIFICATION

|  | Activity | Notes | Date | Done by |
| --- | --- | --- | --- | --- |
| Motor marked |  |  |  |  |
| Motor axle(s) covered |  |  |  |  |
| Sign/plate removed |  |  |  |  |
| Standard specification |  |  |  |  |
| Sandblasted to SA 2.5 |  |  |  |  |
| Epoxy zinc to 75 m |  |  |  |  |
| Polyester resin (stator) 100m |  |  |  |  |
| Epoxy primer 125m |  |  |  |  |
| Top coat 100m |  |  |  |  |
| Metallizing |  |  |  |  |
| Sandblasted to SA 2.5 |  |  |  |  |
| Aluminium 200 m |  |  |  |  |
| Penguard Tie Coat 15 – 30 m |  |  |  |  |
| Waterfine TC 40 – 60 m |  |  |  |  |
| Final treatment |  |  |  |  |
| Sign/plate mounted pursuant to marking |  |  |  |  |
| Axle(s) treated with Tectyl |  |  |  |  |
| Motor surface inspection prior to packing |  |  |  |  |
| Is the motor to be recertified | Yes |  | No |  |
| If yes, sign/plate affixed |  |  |  |  |

- VIBRATION MEASUREMENTS

| Foot motor Flange motor Machine class |  |  |
| --- | --- | --- |
| Measuring point | Zero load | With load |
| 1 |  |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |
| 6 |  |  |

Motor test run with

| Full key |  | Half key |  | No key |  |
| --- | --- | --- | --- | --- | --- |
| With fan |  | With coupling |  |  |  |

- WINDING DATA AC MOTOR

| INSPECTION | Reg 1 | Reg 2 |
| --- | --- | --- |
| Number of slots |  |  |
| Number of spools |  |  |
| Winding type |  |  |
| Number of poles |  |  |
| Jump |  |  |
| No. of wires in parallel |  |  |
| Wire dia |  |  |
| Number of turns per branch |  |  |
| Number of legs per spool |  |  |
| Internal coupling |  |  |
| No. of terminals |  |  |
| Coupling board Y - D - open |  |  |
| Spool head Coupl. Side [mm] |  |  |
| Spool head Not coupl. Side [mm] |  |  |
| Tin dia D1 [mm] |  |  |
| Mean average tooth width t [mm] |  |  |
| Iron under slot B[mm] |  |  |
| Groove depth S [mm] |  |  |
| Length of core without air vents L [mm] |  |  |
| Even branches | Odd branches |  |

- MATERIAL

| Groove card thickness L x B |  | Number |  |
| --- | --- | --- | --- |
| Slot cover (Between slots) L x B |  | Number |  |
| Slot cover top L x B |  | Number |  |
| Lead out sleeve dia and length |  | Number |  |
| Phase card NDE, thickness, L x B |  | Number |  |
| Phase card DE, thickness, L x B |  | Number |  |
| Slot pins L x B |  | Number |  |

- MOTOR DATA

| Manufacturer: |  | RPM |  |
| --- | --- | --- | --- |
| Type |  | Copper weight |  |
| Voltage |  | Thermistors |  |
| Current |  | Heating element |  |
| Frequency |  | Silver weight |  |

- SETTINGS ON WINDING MACHINE:

| Branch | Length | Breadth | Circumference |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |
| 6 |  |  |  |
| 7 |  |  |  |
| 8 |  |  |  |
| 9 |  |  |  |

Registration done by:          			Date:

- BEARING POSITION REPORT

All measurements as deviations in mm from tolerance

|  | Good |  | Meas. by | Must rep | Meas. by |  | Rep | Done by |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Bearing shield |  |  |  |  |  |  |  |  |
| Bearing fit DE1 |  |  |  |  |  |  |  |  |
| Bearing fit ND2 |  |  |  |  |  |  |  |  |
| AXLE |  |  |  |  |  |  |  |  |
| Bearing seat DE 3 |  |  |  |  |  |  |  |  |
| Bearing seat ND 4 |  |  |  |  |  |  |  |  |
| Cast |  |  |  |  |  |  |  |  |
| Axle key DE 5 |  |  |  |  |  |  |  |  |
| Axle key ND 6 |  |  |  |  |  |  |  |  |
| Fan position/- |  |  |  |  |  |  |  |  |
| Fan |  |  |  |  |  |  |  |  |
| Crack test, axle |  |  |  |  |  |  |  |  |
| Seal pos DE |  |  |  |  |  |  |  |  |
| Seal pos ND |  |  |  |  |  |  |  |  |
| HUB position on axle. |  | Before |  |  | Now |  |  |  |

Junction box seen from AS Right    Left      Top

Feed-throughs:

|  | Good | Must rep. | Done date | Done by |
| --- | --- | --- | --- | --- |
| Inspected |  |  |  |  |
| Threads |  |  |  |  |

Maximum temperature (T. Class inspection)

Temperature Cl. -40C + room temperature:     -40 +      =

Highest temperature achieved:

| Date: |  | Done by: |  |
| --- | --- | --- | --- |

  - Assessment of Responsible Persons and Operatives

| Person verified: Organization: ExCB Name: Assessor: |  | Responsible Person/Operative Mark which applies Date. |
| --- | --- | --- |
| Item | Qualifications and work history | Result |
| (1a) | Experience in explosive atmosphere work | Number of years |
| (1b) | Experienced in Ex techniques | “d” “i” “p” “e” “n” “tD” “pD” other Rotating machines Mark which applies Notes |
| (1c) | Working with / assessing engineering drawings | Notes |
| (1d) | Experience with Ex certification requirements/Standards | Notes |
| (1e) | What documents are required for overhaul to remain within certification What records are required? | Notes |
| (1f) | Experience with Ex test requirements | Notes |
| Item | Technical interview |  |
| (2a) | What is a hazardous atmosphere? Explosive Gas , Dust Cloud, Layer of dust, conductive dust and non-conductive dust |  |
| (2b) | Understanding of MSEG, Ignition Temperature, LEL, UEL, Gas groups, Zones 0,1,2 and 20, 21, 22 |  |
| (2c) | Explain where the Ex techniques are used (refer to 1b above for techniques claimed) |  |
| Item | Assessment of skills (see 2b above) |  |
| (3a) | Use of specific mechanical test equipment (shaft/hole diameter, depth, pressure, transfer measurements, flatness, threads, etc) NOTE Overpressure test is mandatory for “d” |  |
| (3b) | Use of specific electrical test equipment (winding resistance, insulation, surface temperature, winding temperature, current, voltage) |  |
| (3c) | Use of calibration status, history Understanding of measurement traceability |  |
| (3d) | Understands what to do if a piece of calibrated equipment is found to be faulty or out of calibration |  |
| (3e) | Can show how test status is maintained throughout the repair/overhaul process |  |

- ADDITIONAL INFORMATION

  - OVER-PRESSURE TEST PROCEDURE

    - INTRODUCTION

There are two methods suitable for the over-pressure test. These are—

- dial gauge measurement; and

- straightedge and feeler gauge measurement.

Typical test rigs for both of these methods are shown in (FIGURE)

    - TEST PROCEDURE

The procedure shall be as follows:

- Check the test piece with the original drawings (that is, the dimensional check). The following faces shall be checked with a straightedge and feeler gauge:

- Flamepaths on enclosure or covers.

- Flat surfaces which will show up on the drawings as the weakest sections of the enclosure.

- For dial gauge measurement (see FIGURE) install dial gauges to surfaces on top, back, front and sides of test piece.

For straightedge and feeler gauge measurement (see FIGURE) draw a line where the straightedge is placed and mark along this line (+) or (-) deformations around the test piece.

Seal the test piece and fill with the testing fluid, taking care that trapped air is minimized. A pressure gauge shall then be fitted to the test piece to check the pressure at the test piece, and also to crosscheck the gauge fitted in the vicinity of the regulator.

Air or gas testing fluid is recommended only for pressurized enclosures, where relatively low pressures are involved.

Apply pressure gradually until the test pressure figure is reached. A safety face shield shall be worn while a visual inspection is made to check for cracks or flaws in the test piece.

The pressure for the over-pressure test shall be held for 1 min for flameproof enclosures and 5 min for pressurized enclosures.

NOTES

1  The pressure to be used for the over-pressure test should be either the value mentioned in the certification documents for such purpose or 1.5 times the reference pressure.

2  If neither the over-pressure test value or the reference pressure test value are known, the values for the pressure test should be:
For Group I, Group II A and B - 1050 kPa (10.5 bar)
For Group II C - 1500 kPa (15 bar)
Remove the pressure source and the testing fluid and open up the test piece for inspection.

3 For dial gauge measurement (see FIGURE) record difference in dial gauge readings.

4 For straightedge and feeler gauge measurement (see FIGURE) place the straightedge on the marked areas and compare to determine the deformation (if any) due to the over-pressure test.

5 For flameproof enclosures, give particular attention to the flamepaths, as these are the most important sections. Flat sections manufactured from steel or metals having a high elongation factor may show minor deformation, but this may not take away from the structural strength of the enclosure. Threaded entries and fasteners should be checked for deformation.

    - REPORTING OF RESULTS

The test shall be considered satisfactory if the enclosure has not suffered structural damage or permanent deformation that may affect its explosion-protection properties.

    - INTERPRETATION OF RESULTS

The extent of permanent deformation reported after overpressure test shall not exceed 0.25 mm per 300 mm when measured with a dial indicator, at the typical points depicted by the following (see FIGURE). This may be taken to be the geographical centre of those parts of the enclosure that are considered to have the least strengthening support.

Permanent deformation is the difference between measurements taken before and after the application of the required pressure test.

Measurements shall be taken at atmospheric pressure.

Where the enclosure area being measured is rectangular, the measurement to be used shall be that across the shortest side. Where this side is greater than 300 mm, the measurement shall be taken across the total length of side and the total amount of deformation shall be calculated from the above requirement.

IMPORTANT
Following the over-pressure test, a test of joint surfaces using a straightedge should result in deviations over any 300 mm length of flange not exceeding one half of the flamepath gap as specified in AS/NZS 60079.1.

FIGURE B1 Example of Over Pressure Test Rig

NOTE: It is permissible to apply pressure to an enclosure prior to the over-pressure test to release stresses and elasticity of a protection type ‘d’ enclosure.

FIGURE B2 TEST POINTS FOR DEFORMATION TESTINGDURING OVER-PRESSURE TEST

  - MACHINING LIMITS

After repair, tests and measurements shall be performed as agreed when the repair work was accepted by the Service Facility.

Where the work involved is confined to machining flameproof surfaces, certification and approval will not be considered invalidated, provided that the cumulative effect of such machining does not—

- reduce the flanges below the minimums where the minimum dimension of the thickness of flanges is detailed in the certification drawings, where available;

- reduce the flange thickness more than 12.5% for internal flanges and 7.5% for external flanges, if nominal only dimensions are detailed in the certification drawings for the thickness of flanges;

- reduce the length of any flamepath whether plain or threaded; or

- result in any deviation to the requirements of the relevant Standards.

Where any flamepath was originally grooved to relieve internal pressure, the grooving shall be machined out and eliminated. This will not be regarded as a modification provided that the conditions required in Items (a), (b), (c) and (e) are satisfied and where explosion pressure tests are carried out in order to determine the new explosion pressure test figure and verify flamepaths.