INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM

FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR

USE IN EXPLOSIVE ATMOSPHERES   (IECEx SYSTEM)

Ex Management Committee, ExMC

TITLE: Report from Mr. John Allen Convenor of ExMC ad hoc WG2 Development of TGD 60079-19

INTRODUCTION

This document is a report from Mr. John Allen Convenor of ExMC ad hoc WG2 Development of TGD 60079-19 and along with draft TGD 60079-19 and is issued for consideration during the ExMC Melbourne Meeting.

Chris Agius

IECEx Secretariat

| Address: SAI Building Level 7 286 Sussex Street Sydney NSW 2000 Australia | Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 e-mail: chris.agius@iecex.com http://www.iecex.com |
| --- | --- |

ExMCWG02Adhoc Report

WG02 Adhoc Members

John Allen (UK) Convenor

Karsten Aleksander Moholt (N)

David Chirdon (USA)

John Waudby (AUS)

Shuchao Li (CHINA)

Title

Development of TGD 60079-19

Purpose

As a result of discussions held during the ExMC Denver 2007 Meetings a sub-group to ExMC WG02 was formed to develop a TGD for IEC 60079-19 Explosive atmospheres - Part 19: Equipment repair, overhaul and reclamation.

Activity

No working group meetings were held, all work was conducted by e-mail.

The convenor would like to note Karston Aleksander Moholt’s valuable contribution to this document prior to his untimely demise on the ill fated Air France flight from Rio de Janeiro to Paris, which crashed on 1st June 2009.

The convenor would like to take this opportunity to thank those working group members that participated for their support.

The TGD for 60079-19 was completed 19th May and sent to IECEx office  & WG2 Convenor on 15th Aug.

Draft Technical Guidance Document

No. IEC.60079-19: Version 1   - xx/xx/2008

IEC 60079-19:2006

2nd  Edition

Explosive Atmospheres –

Equipment repair, overhaul and reclamation

Documentation Control

| Version No. | Date | Changes | Prepared by | Approved by |
| --- | --- | --- | --- | --- |
| 1 | xx xxx 200x | First version | JSA | IECEx Secretariat |

Notes on use of Technical Guidance Documents

TGDs are primarily intended for use by ExCB’s when preparing for assessments. The “Evidence” Colum should be completed by the candidate ExCB under assessment prior to the IECEx Assessment Team visiting the ExCB. prior to the assessment. The assessors will review the completed TGDs and formulate their assessment plan based on the information provided. During the assessment, the assessors will record their findings on the TGDs such that their conclusions regarding the compliance of the body with the IECEx requirements are substantiated.  It is also possible that bodies may wish to use the TGDs for their own self-assessment as part of their on-going self-monitoring. Use by accreditation body assessors is also to be encouraged, provided that the TGDs are not used out of context.

The TGD checklist is structured against the technical requirements of the relevant standard. Each paragraph has a question/activity reflecting the requirement.

Against each question evidence is provided to demonstrate that:-

##### the requirement has been properly understood;

- the way in which conformity with the requirement is to be evaluated is properly documented;

- the conformity evaluation is being implemented effectively in accordance with the documented procedure;

Space is provided for the assessor’s findings to be recorded together with any comments on the evidence provided.

Attention is also drawn to the need for both the candidate ExCB and the IECEx Assessment Team to ensure that the additional requirements of the following Operational Documents are also being met.

- OD 013

- OD 014

- OD 015

This TGD has the following sections:

- Personnel – this is intended to test the certification bodies  personnel’s knowledge of Equipment Repair and their competence to assess the service facility personnel’s competency in Equipment Repair

- Systems – this is provided for the certification body to document all its procedures and guidance material that it uses for assessment and testing of the procedures and processes used by service facilities in Equipment Repair.

- Reclamation and Measuring Equipment – this section is intended for the ExCB to document its procedures and guidance material that it uses identify and record the types of reclamation and testing equipment used by service facilities.  It should include the type of reclamation equipment and calibration status of measuring equipment at the service facility.  Where the service facility intends to sub-contract any reclamations or tests this should be clearly stated. This should include who the reclamations or tests are subcontracted to and how that body will be evaluated for competence.  Evidence should also be provided of the competence of ExCB staff to oversight such contracted reclamations or testing.

TGDs may be used as checklists when conducting an assessment and as a reporting tool to record the findings. The completed TGDs will form part of the document package retained by the IECEx Secretariat with the other papers from each assessment. Handwritten TGDs are acceptable, provided that they are reasonably legible. There is no expectation that an assessor should devote time to transferring a handwritten TGD to an electronic document.

Assessors are encouraged to make suggestions for the improvement of the TGDs so that they remain a useful tool in the assessment process. Suggestions may be made to the Secretariat or directly to the WG2 Convenor. The Secretariat would also be in a position to identify the need for improvements based on studying the completed TGDs submitted by the assessors.

This TGD follows the same clause numbering as IEC 60079-19.  Most of the clauses listed in this TGD contain a comment to assist in the understanding the requirement of the IEC 60079-19 Clause and is shown in italic font

Introduction

Standard No.:  IEC 60079-19: 2006

Title: Explosive atmospheres Part 19: Equipment repair, overhaul and reclamation

Repair philosophy

IEC 60079-19 is supplementary to other relevant IEC standards, for example IEC 60364, as regards installation requirements, and also refers to IEC 60079 and its appropriate parts for the design requirements of suitable electrical equipment.

Part 19 not only gives guidance on the practical means of maintaining the safety and performance requirements of repaired equipment, but also defines procedures for maintaining, after repair, overhaul or reclamation, compliance of the equipment with the provisions of the certificate of conformity or with the provisions of the appropriate explosion protection standard where a certificate is not available.

Clause 4 of this part of IEC 60079 contains general requirements for the repair and overhaul of equipment and should be read in conjunction with the other relevant clauses of this standard dealing with the detailed requirements for individual types of protection. In cases where protected equipment incorporates more than one type of protection, reference should be made to all clauses involved.

The nature of the explosion protection offered by each type of protection varies according to its unique features. Reference should be made to the appropriate standard(s) for details.

Clause 3.2 & 3.6  The relevant (or appropriate) standard means the standard to which the equipment / individual parts  were  originally manufactured

Personnel interviewed (or see Appendix)

| Name | Job title | Abbreviation used in following tables |
| --- | --- | --- |

Other personnel deemed competent (or see Appendix)

| Name | Job title | Abbreviation used in following tables |
| --- | --- | --- |

| IECEx Requirements associated with each Clause of IEC 60079-19 |  |  |  |
| --- | --- | --- | --- |
| Standard | IEC 60079-19:2006 Equipment Repair |  | Doc.No. IECEx TGD .60079-19 |
|  |  |  | Version: 1 |
|  |  |  | Date: xx/xx/2008 |
| Clause | Understanding Shown of the Following Requirements | Evidence from body under assessment (completed by candidate ExCB, prior to assessment) | Comments by IECEx Assessor |
| Intro-duction | Ignition mechanisms Describe the relationship of IEC 60079-19 with regards to other IEC standards |  |  |
| 3 | Terms & definitions |  |  |
| 4 | General |  |  |
| 4.1 | General Principles Repair to certification documents or repair using manufacturer’s spare parts = full compliance Repair to protection type standard & 79-19 = compliance with type std not certification documents Repair not in compliance with 79-19 verify suitability |  |  |
| 4.2 | Statutory Requirements Awareness of relevant national legislation which may govern repair & overhaul of Ex equipment |  |  |
| 4.2.1 | Repair facility |  |  |
| 4.2.2 | User |  |  |
| 4.3 4.3.1 4.3.2 4.3.4 | Instruction to the user Records & work instructions Re-installation of repaired equipment Repair facilities |  |  |
| 4.4 | Instructions for the repair facility |  |  |
| 4.4.1 | Repair & overhaul |  |  |
| 4.4.1.1 | General |  |  |
| 4.4.1.1 Para. 1 | QMS Repair facilities shall operate a Quality Management System that meets with the requirements of the ISO 9000 series of standards (refer to OD 014) |  |  |
| 4.4.1.1 Para 2 | Responsible Person The repair facility shall appoint a person ('Responsible Person') with the required competency (see Annex B), within the management organization, to accept responsibility and authority for ensuring that the overhauled/repaired equipment complies with the certification status agreed with the user |  |  |
|  | - R P Competency Competency requirements specified in Annex B i.e. 3rd party Assessment of Competency in IEC 60079-19 to ISO 17024 or assessed as Annex B to ISO 17024 during audit |  |  |
|  | - R P Responsibility & Authority OD 014 1.5 |  |  |
| 4.4.1.1 Para 3 | Adequate facilities The repair facility must have adequate repair and overhaul facilities as well as the appropriate equipment necessary, taking into account the specific type of protection. JSA Note i.e. - Mechanical handling capability - Rewind capability - Machining capability - Measuring capability - Test capability - Recovery process’s |  |  |
| 4.4.1.1 Para 3 | Adequate facilities continued - Operator competency e.g. Recovery process Electrical rewind Machine shop Electrical/mechanical fitter Electrical/electronic repair |  |  |
| 4.4.1.1 Para 3 | Ex Operatives The repair facility must have adequate trained Operatives with the required competency (see Annex B) and authority to carry out the activities, taking into account the specific type of protection. JSA Note: i.e. Operators are persons making measurements or decisions which can affect the certification status of Ex Equipment working under the RP’s authority - Ex Operator competency Competency requirements specified in Annex B (Refer to OD 015 for guide on determining competence level) |  |  |
| 4.4.1.1 Para 4 | Assessment of equipment status The repair facility shall conduct an assessment of the status of the equipment to be repaired, agree with the user the expected certification status of the equipment after repair and the scope of work to be done - Assessment Report |  |  |
| 4.4.1.1 Para 4 | Repaired equipment certification status agreed with user i.e. Repair to certification docs or Repair to protection type standard |  |  |
| 4.4.11 Para 4 | Omission of tests The omission of any tests mentioned within 60079-19 that the user could reasonably assume to be included to be agreed with the user |  |  |
| 4.4.1.1 Para 4 | Responsible Person competency The Responsible Person shall only conduct assessments with the explosion protection techniques for which he has demonstrated his competence (i.e. is the R P competent for the range of protection types in service facility scope) i.e. Facility scope v RP Competency (Refer to OD 015 for guide on determining competence level) |  |  |
| 4.4.1.1 Para 5 | Work external to repair facility The repair facility shall include procedures and systems to carry out overhaul/repair work at sites external to the repair facility, where appropriate |  |  |
| 4.4.1.2 | Certification and standards The repairer’s attention is directed to the need to be informed of, and to comply with, the relevant explosion-protection standards and certification requirements applicable to the equipment to be repaired or overhauled |  |  |
| 4.4.1.3 | Competency - All operators Those operatives directly concerned with the repair and/or overhaul of the certified equipment are trained, experienced, skilled, knowledgeable and/or supervised on this type of work |  |  |
| 4.4.1.3 Para 1 | Competency assessment Competency assessments ( Ex operators) as specified in Annex B (also OD 015) |  |  |
| 4.4.1.3 Para 3 | Assessment interval Appropriate training and assessment shall be undertaken from time to time at intervals depending on the frequency of utilization of the technique or skill and change of standards or regulations. The interval should normally not exceed three years. |  |  |
| 4.4.1.4 | Testing Should it prove impracticable to carry out certain tests, e.g., a component of a complete equipment taken off site for repair such as a rotor of a rotating machine, the repairer shall, before putting the repaired equipment back into service, ascertain from the user or manufacturer the consequences of omitting such tests. Note; In some countries, legal consequences may depend upon the extent to which the carrying out or not of certain actions or tests is practicable. |  |  |
| 4.4.1.5 | Documentation |  |  |
| 4.4.1.5.1 Para 1 | General The repair facility should seek to obtain all necessary information/data from the manufacturer or user for the repair and/or overhaul of the equipment. This may include information relating to previous repairs, overhauls or modifications. |  |  |
| 4.4.1.5.1 Para 1 | Explosion protection standards Should also have available and refer to the relevant explosion-protection standard |  |  |
| 4.4.1.1 Para 2 | Data The data available for the repair and/or overhaul should include but need not be limited to, details of the:- – technical specification; – drawings; – explosion protection performance and conditions of use; – dismantling and assembly instructions; – certificate limitations (special conditions for safe use), where specified; – marking (including certification marking); – recommended methods of repair/overhaul for the equipment; – list of spare parts - Special Conditions of Use Where an X is attached to the certificate number , the Condition of Use must be read to meet certification requirements – Reduced Gaps etc |  |  |
| 4.4.1.5.1 Final Para | Explosion protection standard document control The repair facility shall maintain controlled copies of any relevant explosion protection standards with which repaired/overhauled equipment is claimed to comply. |  |  |
| 4.4.1.5.2 Para 1 | Job Report to the User At the completion of the work, job reports shall be submitted to the user (see 4.3.2) containing, at least, the following: – details of fault detected; – full details of repair and overhaul; – list of replaced or reclaimed parts; – results of all checks and tests (in sufficient detail to be useful if required by the next repairer, see 4.3.2); – summary of previous history of the repaired product including information as gathered under 4.3.2; – copy of the user contract or order |  |  |
| 4.4.1.5.2 Para 3 | Job Report Retention Shall be retained for a period of time as agreed with the user (IECEx requires 10 Years). Retained information shall be adequately controlled to ensure correct retrieval. |  |  |
| 4.4.1.5.3 Para 1 1st - | Repair Facility Records The following records shall be retained by the repair facility for 10 years - Technical Standards current and past copies of relevant Technical Standards |  |  |
| 4.4.1.5.3 Para 1 2nd - | - QMS Records 1) details of Repair provider's Quality Assessment Scheme; 2) test instrument calibration; 3) competency and training records of personnel; 4) purchasing control system; 5) customer complaints system; 6) internal and, where appropriate, external audit documentation; 7) management review; 8) process control procedures; 9) register of manufacturer’s drawings |  |  |
| 4.4.1.5.3 Para 1 3rd - | - Job Records 1) the steps taken to obtain the certification documents; 2) mechanical inspection record for compliance with relevant standards; 3) defect identification; 4) electrical test records before and after repair including traceability of instruments used and pass/fail criteria; 5) certificates of conformity for replacement components; 6) recovery procedure for repaired components; 7) record of mechanical inspection during assembly and upon completion; 8) record of work undertaken by the repair facility. |  |  |
| 4.4.1.5.3 Para 2 | - Reclamation Records a) a detailed justification for the work carried out; b) various options considered (e.g., welding, metal spraying); c) technical parameters, e.g., bond strength; d) the reasons for selecting the chosen technique; e) consumables used and method of storage; f) base material; g) manufacturers’ instructions considered; h) procedure utilized; i) identity and competency of the operator; j) inspection procedure used, e.g., ultra-sonic, dye-penetration, X-ray; k) maintenance and calibration details of automatic systems. |  |  |
| 4.4.1.5.3 Para 3 | Record Retention These records shall be retained for a period of at least ten years or as agreed with the user. OD 014 1.4 B Records must also be kept of Ex Equipment that, even after being services, do not comply and are not marked with the R-Label |  |  |
| 4.4.1.6 | Spare Parts |  |  |
| 4.4.1.6.1 | General It is preferable to obtain new parts from the manufacturer, and the repairer shall ensure that only appropriate spare parts are used in the repair or overhaul of certified equipment. Depending on the nature of the equipment, these spare parts may be identified by the manufacturer, the equipment standard or the relevant certification documentation. |  |  |
| 4.4.1.6.2 | Sealed Parts Parts, which are required by the equipment specification and certificate documents to be sealed, shall be replaced only by the particular spare part(s) detailed in the parts list. |  |  |
| 4.4.1.7 | Identification of Repaired Equipment |  |  |
| 4.4.1.7 Para 1 | Equipment shall be marked The equipment shall be marked to identify the repair or overhaul and the repairer's identity. The marking for the repaired equipment is given in Annex A. |  |  |
| 4.4.1.7 Para 2 | Service Facility Label Marking may be provided on a separate label. It may be necessary to amend or remove or supplement the label in certain circumstances as follows. |  |  |
| 4.4.1.7 Para 2a | Certification label removal If after repair, overhaul or modification, an equipment is changed such that it no longer conforms with the standard and certificate (see 3.11), the certification label shall be removed unless a supplementary certificate has been obtained. |  |  |
| 4.4.1.7 Para 2b | Compliance with protection standard - R in inverted triangle If the equipment is changed during repair or overhaul so that it still complies with the restrictions imposed by this standard and the explosion protection standards to which it was manufactured, but does not necessarily comply with the certificate, the certification label should not normally be removed and the repair symbol "R" shall be written within an inverted triangle (see Annex A). |  |  |
| 4.4.1.7c | Assessment to current type standard - Competent Assessor Where the standards to which the previously certified equipment was manufactured are not known, the requirements of this standard and the current edition of the relevant explosion protection standards shall apply. An assessment, by a person competent in assessing explosion protected equipment, shall be conducted to verify compliance with the relevant level of safety prior to release of the equipment by the repairer |  |  |
| 4.4.2 | Reclamations |  |  |
| 4.4.2.1 | General Reclamations not affecting the explosion protection are not the subject of this sub-clause. Such parts should be reclaimed using good engineering practices. Where the repair process involves reclamation work, then, in addition to the requirements of 4.4.1 for repairs and overhauls, the requirements of 4.4.2 also apply. |  |  |
| 4.4.2.2 | Exclusions Some component parts are considered not to be reclaimable and are therefore excluded from the scope of this standard, such as: – component parts made from the following materials: glass, plastics, or any material that is not dimensionally stable; – fasteners; – component parts, e.g., some encapsulated assemblies, which have been stated by the manufacturer to be not subject to repair. |  |  |
| 4.4.2.3 | Requirements |  |  |
| 4.4.2.3.1 | General Any reclamation shall be carried out by competent personnel, skilled in the process to be employed and using good engineering practices |  |  |
| 4.4.2.3.1 Para 1 | - Reclamation operator competency& test interval Operators of reclamation techniques, e.g. welding, metal spraying, shall be required to undertake a practical skill test in the technique before being permitted to utilize the technique for the first time and every three years thereafter. |  |  |
| 4.4.2.3.1 Para 1 | - Skill test Metal spray requirement specified in bond strength therefore skill test must metal spray test piece and measure bond strength Welding requirements not specified but typically would include test piece, visual inspect, NDT inspect, section & detailed inspection for penetration |  |  |
| 4.4.2.3.1 Para 1 | - Continuity of practice If the operator has not used the technique in the previous six months, he shall undertake a re-test. |  |  |
| 4.4.2.3.1 Para 2 | Propriety processes If any proprietary process is used, the instructions of the originator of such a process should be followed. |  |  |
| 4.4.2.3.1 Para 3 | Reclamation record In addition to 4.4.1.5.3. Para2 All reclamation shall be properly documented and records retained. Such records include: – identification of the component part; – method of reclamation; – detail of any dimensions which differ from those in relevant certification documents or the original dimensions of the component part; – drawing showing reclamation details including material removed and replaced; – date; – name of the organization carrying out the reclamation. |  |  |
| 4.4.2.3.1 Para 4 | User reclamation record If the reclamation is carried out other than by the user, the user shall be provided with a copy of the record. |  |  |
| 4.4.2.3.1 Para 5 | Reclamation results in assessment to protection type standard - R in inverted triangle A reclamation procedure which would result in dimensions affecting explosion-protection integrity being different from those given in relevant certification documents may be permissible if such changed dimensions still meet the requirements of the restrictions imposed by this standard and the explosion protection standards to which it was manufactured. The certification label should not be removed and the repair symbol "R" shall be written within an inverted triangle. Same as 4.4.1.7b |  |  |
| 4.4.2.3.1 Para 5 | Assess to current standard Where the standards to which the previously certified equipment was manufactured are not known, the requirements of this standard and the current edition of the relevant explosion protection standard shall apply. An assessment, by a person competent in assessing explosion protected equipment shall be conducted to verify compliance with the relevant level of safety prior to release of the equipment by the repairer. Same as 4.4.1.7c |  |  |
| 4.4.2.3.1 Para 6 | In event of uncertainty In the event of any uncertainty regarding the permissibility, from an explosion-protection safety point of view, of an intended reclamation procedure, the advice of the manufacturer or certifying authority should be sought. It may also be necessary to carry out tests to verify that the reclamation procedure is acceptable. |  |  |
| 4.4.2.3.2 | Responsibilities If reclamations are contracted out by the repair facility to a specialized industry, such reclamations shall be the responsibility of the repair facility. - Sub-contracted reclamations - Sub-contractor’s (S-C) QMS - S-C recovery process - S-C process control - S-C operator competency - S-C operator skill test - S-C reclamation records |  |  |
| 4.4.2.4 | Reclamation Procedures |  |  |
| 4.4.2.4.1 | General The following outlines some of the reclamation procedures which may be applicable to explosion-protected equipment. It should be recognized that not all procedures are applicable to all types of protection. Detailed instructions are given in the appropriate clauses of this standard. |  |  |
| 4.4.2.4.1 Para 3 | Minimum metal removal Metal removal shall be minimized and be just sufficient to remove the defect requiring repair and provide the minimum coating thickness recommended for the technique used. |  |  |
| 4.4.2.4.1 Para 3 | Industry Guidance Industry guidance would suggest that the removal of up to 2 % of metal thickness for metal spraying and up to 20 % for welding will not be significantly detrimental to the strength of the component. Note from JSA On small diameter shafts (<50mm) the max 2% metal removal for metal spray is a problem and this is being addressed in Ed 3 of IEC 60079-19 |  |  |
| 4.4.2.4.1 Para 3 | Greater metal removal than industry guidance On small diameter shafts (<50mm) the max 2% metal removal for metal spray is a problem and this is being addressed in Ed 3 of IEC 60079-19 |  |  |
| 4.4.2.4.1 Para 4 | Reclamation completion record On completion of the reclamation, the repairer shall satisfy himself that the equipment is in a fully serviceable condition and complies with the standard(s) for the type of protection. Such compliance shall be recorded by the repair facility and retained in the job files. |  |  |
| 4.4.2.4.2 | Metal Spray This method shall be used only when the extent of the wear or damage, plus the machining necessary to prepare the component part for reclamation, does not weaken the part beyond safe limits. A sprayed metal inlay, whilst adding some stiffness, should not be taken into account when strength is considered. Indeed, the machining process prior to the application of metal spray may introduce stress raisers which may further weaken the component. Metal spraying is not recommended for some high-speed and large-diameter applications; it is only acceptable where the materials are metallurgically compatible and the parent base metal is free from defects. Note from JSA Metal spray materials do not need to be metallurgically compatible this is being addressed in Ed 3 of IEC 60079-19 |  |  |
| 4.4.2.4.2 | Metal spraying continued Metal spray techniques from JSA - Thermal powder - lower bond strength - Thermal wire – lower bond strength - Twin wire arc – higher bond strength - Plasma – higher bond strength - Diamond Jet - higher bond strength - HVOF High Velocity Oxy/Fuel - highest bond strength |  |  |
| 4.4.2.4.3 | Electroplating Electroplating is an acceptable procedure provided that the part is not weakened beyond safe limits. Detailed procedures for chromium and nickel plating are given in ISO 6158 and ISO 4526, respectively. |  |  |
| 4.4.2.3.4 | Sleeving This method shall be used only when the extent of the wear and damage, plus the machining necessary to prepare the part for reclamation, does not weaken the part beyond safe limits. A sleeve, whilst adding some stiffness, should not be taken into account when strength is considered |  |  |
| 4.4.2.4.5 | Brazing & Welding Reclamation by brazing or welding shall be considered only if the technique employed ensures the correct penetration and fusion of braze or weld with parent metal, resulting in adequate reinforcement, the prevention of distortion, the relief of stresses and the absence of blow-holes. It should be recognized that brazing and welding raise the temperature of the component to a high level and may cause fatigue cracks to propagate. |  |  |
| 4.4.2.4.5 Para 1 | Brazing Techniques Note from JSA Micro flow braze for reclamation of small flamepath surface defects |  |  |
| 4.4.2.4.5 Para 2 | Welding techniques The following welding techniques are recognised by this standard: – MMA: Manual Metal Arc – MIG: Metal Inert Gas – TIG: Tungsten Inert Gas – Sub-Arc: MIG under a layer of flux – Hot wire |  |  |
| 4.4.2.4.5 Para 3 | Other welding techniques Other techniques shall only be utilized in reclamations after due consultation with the manufacturer or, if relevant, the certifying authority. |  |  |
| 4.4.2.4.6 | Metal Stiching The cold reclamation of a fractured casting by the technique of closing the fracture with nickel alloy stitches and sealing the crack by nickel alloy chain studding may be admissible subject to a suitable thickness of casting. |  |  |
| 4.4.2.4.7 | Machining of stator & rotor core Damaged stator or rotor cores shall not be machined to remove surface irregularities without reference to the manufacturer to ascertain the maximum permissible air gap which shall not be exceeded Note from JSA Machining to remove a hot spot on a rotor minimal metal removal at hot spot not along the full length of rotor |  |  |
| 4.4.2.4.8 | Threaded holes for fasteners Threads which have been damaged beyond an acceptable extent may be reclaimed, depending upon the type of protection, by the following means: |  |  |
| 4.4.2.4.8 | Threaded hole recovery techniques – oversize drilling and re-tapping; – oversize drilling, re-tapping and the fitting of a proprietary thread insert which passes the appropriate pull test as specified by the thread insert manufacturer; – oversize drilling, plugging 1, re-drilling and re-tapping; – plugging 2, re-drilling and tapping elsewhere; – plug-welding, re-drilling and tapping. 1 & 2 Plugs shall be securely retained. |  |  |
| 4.4.2.4.9 | Re-machining Re-machining worn or damaged surfaces shall be considered only if – the component part is not weakened beyond safe limits; – provided that the integrity of the enclosure is maintained; – the required surface finish is achieved. |  |  |
| 4.4.3 | Modifications |  |  |
| 4.4.3 Para 1 | Repair includes modification Where the repair process involves modification work, then, in addition to the requirements of 4.4.1 for repairs and overhauls, the requirements of 4.4.3 also apply. |  |  |
| 4.4.3 Para 2 | Permitted modification No modification shall be made to the certified equipment unless that modification is permitted in the certificate or is approved in writing by the manufacturer. Subsequent clauses of this standard give detailed instructions regarding modifications in the context of different types of protection. |  |  |
| 4.4.3 Para 3 | Non conforming modification Where a modification is proposed which would result in the equipment not conforming with the certification documents and the relevant type of protection standards, the user shall be informed in writing that the equipment is no longer suitable for use in an explosive atmosphere, and his written instructions obtained. If the proposal is carried out, the certification label shall be removed or altered to give a clear indication that the equipment is not certified |  |  |
| 4.4.4 | Temporary Repairs |  |  |
| 4.4.4 Para 1 | Temporary repair A temporary repair intended to achieve continued short-term operation of the equipment shall only be carried out if retention of explosion-protection aspects is ensured or other appropriate measures are taken until the equipment is fully restored. Certain temporary repair procedures may therefore not be allowed. Any temporary repair shall be brought up to full repair standards as soon as reasonably |  |  |
| 4.4.5 | Removal of damaged windings |  |  |
| 4.4.5 Para 1 | Acceptable method The procedure of softening the impregnating varnish of windings with solvents before stripping is acceptable. Note from JSA This process is rarely used for environmental, occupational H&S & response time reasons and is not effective for epoxy impregnated windings |  |  |
| 4.4.5 Para 2 | Alternative method - heating The alternative procedure which uses the application of heat to facilitate the removal of windings is acceptable provided that the operation is carried out with caution so as not to affect significantly the insulation between the laminations of magnetic parts. Particular caution is necessary, and if in doubt, the advice of the manufacturer will be sought regarding the construction of the core and the inter-laminar insulation material with respect to equipment with type of protection "e" and equipment with any type of protection having temperature class T6, T5 or T4. |  |  |
| 4.4.5 Para 3 | Particular caution Ex e The need for particular caution in those circumstances arises from the fact that an increase in core loss, which could result from degradation of inter-laminar insulation, could significantly affect type "e" parameters (tE-time, etc.) or result in the temperature classification being exceeded. |  |  |
| 4.4.5 Para 3 | Equipment in serviceable condition The repairer shall satisfy himself, as in all reclamation procedures, that on completion of the reclamation the equipment is in a fully serviceable condition and complies with the standard(s) for the relevant explosion concept (see also 4.4.2.4). |  |  |
| 4.4.6 | Inverters |  |  |
| 4.4.6 Para 1 | Care with inverters Particular attention is drawn to the need for care when adding an inverter to an Ex-rotating machine in ensuring that this is only done when the intended combination of inverter and rotating machine is specified in the certificate or in the rotating machine manufacturer's documentation. Third-party repairers should use special care to establish that any inverter on which they are asked to work is so specified. |  |  |
| 5 | Additional requirements Ex d |  |  |
| 5.1 | Application Equipment with type of protection "d". It should be read in conjunction with Clause 4, which contains general requirements, and any other appropriate clauses if relevant. The relevant equipment standards which should be referred to when repairing or overhauling an Ex "d" equipment are those to which the equipment was originally manufactured (see IEC 60079-1). |  |  |
| 5.2 | Repair and overhaul |  |  |
| 5.2.1 | Enclosures It is preferable to obtain new parts from the manufacturer. Particular attention shall be paid to the correct assembly of flameproof enclosures after repair or overhaul, in order to ensure that the flameproof joints comply with the requirements of the standard and, where appropriate, with the certification documents. Where flameproof joints are not gasketed, they may be protected by the use of grease, non-setting sealing compound or non-hardening tape applied externally in accordance with IEC 60079-14. |  |  |
| 5.2.1 Cont. | Gaskets Where gaskets which are not part of the flamepath are incorporated into the flameproof joints, replacements shall be of the same materials and dimensions as the original. Any proposed change of material shall be referred to the equipment manufacturer, user or certification authority. |  |  |
| 5.2.1 Cont. | Drilling holes The drilling of holes into an enclosure is a modification and shall not be carried out without reference to the manufacturer's certified drawings, or, in exceptional circumstances, e.g., manufacturer discontinued trading, to the certifying authority. |  |  |
| 5.2.1 Cont. | Surface finish Care shall be taken when changing surface finish, paint, etc., as this may affect the surface temperature of the enclosure and thus the temperature classification. Note from KAM; For installations in corrosive environments the original surface coating is often not adequate. More appropriate surface coatings should be discussed with the manufacturer, if possible, and customer |  |  |
| 5.2.1 Cont. | Before returning to service Before a rewound or repaired rotating machine is put back into service, it is essential to ensure that fan cover ventilation holes are not blocked or damaged so as to impair the passage of cooling air over the machine, and that any fan clearances are in compliance with the requirements of the equipment standards, if appropriate. Should a fan or fan cover be damaged so as to require renewal, the replacement parts shall be obtained from the manufacturer. If unobtainable, then they shall be of the same dimensions and at least the same quality as the original parts. They shall, where appropriate, take account of the requirements of the equipment standard to avoid frictional sparking and electrostatic charging, and of the chemical environment in which the machine is used. |  |  |
| 5.2.2 | Cable and conduit entries Entries into flameproof enclosures shall conform, after repair or overhaul, to the conditions detailed in the appropriate equipment standard and/or certification documents where applicable |  |  |
| 5.2.3 | Terminations Care shall be taken when refurbishing terminations to maintain clearance and creepage distances. Any replacement terminals, bushings or parts should be obtained from the manufacturer or shall conform to the relevant equipment standard and/or certification documents, where applicable. |  |  |
| 5.2.4 | Insulation A class of insulation the same as, or superior to, that originally provided may be employed, e.g., a winding insulated with class E material may be repaired using class F material (see IEC 60085). |  |  |
| 5.2.5 | Internal connections There are no particular requirements relating to this type of protection but repairs to internal connections shall be of a standard at least equivalent to that of the original design. |  |  |
| 5.2.6 | Windings |  |  |
| 5.2.6.1 | General The original winding data shall preferably be obtained from the manufacturer. If this is not reasonably practicable then use may be made of copy winding techniques. The materials used in rewinding shall comprise an appropriate insulation system. If superior insulation is proposed compared to that of the original, the rating of the winding shall not be increased without reference to the manufacturer, as the temperature classification of the equipment could then be adversely affected. |  |  |
| 5.2.6.2 | Repair of rotating machine rotors Faulty die-cast aluminium rotor cages shall be replaced by new rotors obtained from the manufacturer or his distributor. Bar-wound cage rotors may be rewound using similar materials of identical specification. Particular care is necessary to ensure that, when replacing conductors in a cage rotor, such conductors are tight in the slots. The method of achieving tightness employed by the manufacturer should be adopted. |  |  |
| 5.2.6.3 | Testing after repair of windings |  |  |
| 5.2.6.3.1 | General Windings, after complete or partial repair, shall be subjected, preferably with the equipment assembled, to the following tests, as far as is reasonably practicable. |  |  |
| 5.2.6.3.1 Cont. | - Winding resistance test The resistance of each winding shall be measured at room temperature and verified. In the case of three-phase windings, the resistance of each phase or between line terminals shall be balanced. Unbalance (i.e. the difference between the highest and the lowest values) shall be less than 5 % of middle value. |  |  |
| 5.2.6.3.1 Cont. | - Insulation resistance test An insulation resistance test shall be applied to measure the resistance between the windings and earth, between windings where possible, between windings and auxiliaries, and between auxiliaries and earth. A minimum test voltage of 500 V d.c. is recommended. Minimum acceptable insulation resistance values are a function of rated voltage, temperature, type of equipment and whether the rewind is partial or complete. NOTE The insulation resistance should not be less than 20 MΩ at 20 °C on a completely rewound equipment intended for use up to 690 V. |  |  |
| 5.2.6.3.1 Cont. | - High voltage test A high-voltage test, in accordance with a relevant equipment standard, shall be applied between windings and earth, between windings where possible, and between windings and auxiliaries attached to the windings. |  |  |
| 5.2.6.3.1 Cont. | - Rated voltage test The transformer or similar equipment shall preferably be energized at rated supply voltage. The supply current, secondary voltage and current shall be measured. The measured value shall be compared with that derived from the manufacturer's data, where available, and in three-phase systems should be balanced in all phases, as far as is reasonable. |  |  |
| 5.2.6.3.1 Cont. | - High voltage equipment High-voltage (for example, 1 000 V a.c./1 500 V d.c. and above) and other special equipment may require additional tests. This shall be the subject of the repair or overhaul contract. |  |  |
| 5.2.6.3.2 | Rotating machines In addition to the above tests, rotating machines shall be subjected to the following tests so far as is reasonably practicable. |  |  |
| 5.2.6.3.2 Cont. | - No load test The machine shall be run at full speed and the cause of any untoward noise and/or mechanical vibration investigated and corrected. |  |  |
| 5.2.6.3.2 Cont. | - Locked rotor test The stator windings of cage machines shall be energized at an appropriate reduced voltage, with the rotor locked, to obtain between 75 % and 125 % of full-load current and to ensure balance on all phases. (The test, which in some respects is an alternative to a full load test, is used to confirm the integrity of the stator winding and its joints and to indicate the presence of rotor defects.) Unbalance shall be less than 5 % of the middle value. |  |  |
| 5.2.6.3.2 Cont. | - High voltage test High-voltage (for example, 1000 V a.c./1 500 V d.c. and above) and non-cage machines may require alternative and/or additional tests. This shall be the subject of the repair or overhaul contract. NOTE Guidance on test voltages and additional tests for rotating machines is given in IEC 60034. |  |  |
| 5.2.6.4 | Temperature sensors If temperature sensors are included to monitor winding temperatures, it is recommended that they are embedded in the winding before varnishing and curing. |  |  |
| 5.2.7 | Auxiliary equipment |  |  |
| 5.2.7.1 | Flameproof brake units Where a flameproof brake unit attached to a rotating machine is also certified and is in need of repair, it is recommended that it be returned to the manufacturer, together with the machine. This course is recommended because of the close construction constraints. However, such repairs are possible by repair facilities other than those of the manufacturer providing the repair facility is in possession of the necessary drawings and information from the manufacturer. |  |  |
| 5.2.7.2 | Other auxiliary devices Where auxiliary devices are based on different types of protection, the corresponding clauses of this standard shall be consulted before any repairs are undertaken. |  |  |
| 5.2.8 | Light-transmitting parts No attempt shall be made to re-cement or repair light-transmitting parts, and only complete replacement assemblies, as specified by the manufacturer, shall be used. Light-transmitting or other parts made from plastics shall not be cleaned with solvents. Household detergents are recommended for this purpose. |  |  |
| 5.2.9 | Encapsulated parts In general, encapsulated parts (e.g. switching devices) are not considered suitable for repair. |  |  |
| 5.2.10 | Batteries Where batteries are used, the manufacturer's advice shall be followed. |  |  |
| 5.2.11 | Lamps Lamp types specified by the manufacturer shall be used as replacements and the maximum wattage specified shall not be exceeded. NOTE The position of a reflector, if any, or the distance between the lamp and the window should be maintained. |  |  |
| 5.2.12 | Lampholders Replacements listed by the manufacturer shall be used. |  |  |
| 5.2.13 | Ballasts Chokes or capacitors shall be replaced only by the manufacturer's listed parts, unless reference is made to the manufacturer to determine if alternatives may be used. |  |  |
| 5.3 | Reclamation Reclamations using the techniques detailed in 4.4.2 may be used with type of protection "d" equipment subject to the following restrictions of this clause. |  |  |
| 5.3.1 | Enclosures |  |  |
| 5.3.1.1 | General Reclaimed component parts of flameproof enclosures should be used only if they pass, when appropriate, the applicable over-pressure test. Metal stitching shall not be used. |  |  |
| 5.3.1.1 Cont. | Damage to non flameproof parts Damage to components which are not an integral part of the flameproof enclosure, for example, fixing lugs, may be repaired by welding or metal stitching but care should be taken to ensure that the integrity and stability of the equipment is not impaired. It is particularly important to check that any cracks being repaired do not extend to the flameproof enclosure. |  |  |
| 5.3.1.1 Cont. | Welding efficacy The efficacy of reclaiming or repairing by the technique of welding may be further compounded by considerations of different base materials, for example, aluminium or steel. If uncertainty exists, the repairer shall seek advice, preferably from the manufacturer, before this technique is adopted. Welding of cast-iron flameproof enclosures is not permitted without the approval of a metallurgical expert. |  |  |
| 5.3.1.2 | Flameproof joints Damaged or corroded flameproof joint faces should be machined, after consultation with the manufacturer wherever possible, only if the resultant joint gap and flange dimensions are not affected in such a way that they contravene the certification documents. If the certification documents are not available, further guidance shall be taken from Annex C. |  |  |
| 5.3.1.2 Cont. | - Flanged joints Welding, electroplating and re-machining flanged joint faces may be permissible, having due regard to the limitations of the technique (see Clause 4). The use of metal-spraying techniques is permissible provided the bond strength is greater than 40 MPa. |  |  |
| 5.3.1.2 Cont. | - Spigoted/cylindrical joints Machining the male part will require addition of metal to it, and also machining of, the female part (or vice versa), thus ensuring that the flamepath dimensions comply with the equipment standard, and where appropriate the certification documents. If only one part is damaged, that part may be restored to its original dimensions by the addition of metal and re-machining. The addition of metal may be by electroplating, sleeving or welding, but metal spraying techniques which have a bond strength less than 40 MPa are not recommended. |  |  |
| 5.3.1.2 Cont. | - Threaded joints i) Cable and conduit entries: It is not recommended that damaged male threaded parts be reclaimed; new components shall be used. Damaged female threads may be reclaimed using MMA, MIG and TIG welding techniques. ii) Screwed covers: Reclamation of the threaded parts of screwed covers and of the associated housings may be possible utilizing MMA, MIG and TIG welding techniques. |  |  |
| 5.3.1.3 | Threaded holes for fasteners Reclamation of damaged threaded holes shall be carried out using the techniques described in 4.4.2.4.8 taking into account the requirements given in 5.3.1.1. |  |  |
| 5.3.2 | Sleeving Care should be taken not to introduce an additional effective flamepath. The sleeve shall be securely retained. |  |  |
| 5.3.3 | Shafts and housings Shafts and bearing housings, including flameproof joints, may be reclaimed by the use of electroplating, metal spraying, sleeving or welding (except MMA) techniques. Any subsequent machining shall be to the flamepath dimensions as specified in the equipment standard and/or certification documents, as appropriate. If the certification documents are not available, further guidance shall be taken from Annex C. Welding may be appropriate having due regard to the limitations of this technique (see 4.4.2.4.5). |  |  |
| 5.3.4 | Sleeve bearings Sleeve-bearing surfaces may be reclaimed by electroplating, metal spraying or welding (except MMA) techniques. |  |  |
| 5.3.5 | Rotors and stators If rotors and stators are to be lightly skimmed to remove eccentricities and surface damage then the resultant increased air gap between rotor and stator should not produce, for example, a change in pressure-piling characteristics or a change in higher external surface temperatures that infringe the temperature class of the machine. If uncertainty exists with regard to possible decrimental effects, the repairer shall seek advice preferably from the manufacturer before this procedure is adopted. |  |  |
| 5.3.5 Cont. | Core flux test Skimmed or damaged stator cores shall be submitted to a "flux test" to ensure that there are no remaining hot spots which could infringe the temperature classification or cause subsequent damage to the stator windings. |  |  |
| 5.4 | Modifications |  |  |
| 5.4.1 | Enclosures No modification affecting the explosion protection shall be carried out on parts of a flameproof enclosure without reference to the certification documentation and/or the manufacturer or, in exceptional circumstances, for example, the manufacturer discontinued trading, with the certifying authority. |  |  |
| 5.4.2 | Cable or conduit entries Additional entries shall not be made without reference to the certification documentation and/or the manufacturer or, in exceptional circumstances, for example, the manufacturer discontinued trading, with the certifying authority. |  |  |
| 5.4.2. Cont. | Indirect entry Indirect entry, where the external conductors are connected by means of a plug and socket or within a terminal box, shall not be changed to direct entry, i.e., where the external conductors and cables are connected within the main enclosure. |  |  |
| 5.4.3 | Terminations Termination assemblies containing a flameproof joint shall not be modified, for example, terminals with bushings between indirect-entry terminal box and main enclosure. Termination assemblies not containing a flameproof joint may be replaced by alternatives of adequate design and construction in terms of numbers, current-carrying capacity, creepage and clearance distances, and quality. |  |  |
| 5.4.4 | Windings Change of voltage If equipment is to be rewound for another voltage, reference shall be made to the manufacturer. In such cases it shall be ensured that, for example, the magnetic loading, current densities, losses are not increased, appropriate new creepage and clearance distances are observed and the new voltage is within the limits of the certification documents. The rating plate shall be changed to show the new parameters. |  |  |
| 5.4.4. Cont. | Change of speed Rewinding a rotating machine for a different speed shall not be carried out without reference to the manufacturer, since the electrical and thermal characteristics of the machine could be significantly altered to the point of being outside the limits imposed by the assigned temperature class. |  |  |
| 5.4.5 | Auxiliary equipment In cases where additional auxiliary equipment is requested, for example, anti-condensation heaters or temperature sensors, the manufacturer shall be consulted to establish the feasibility of and the procedure for the proposed addition. |  |  |
| 6 | Additional requirements for the repair and overhaul of equipment with type of protection "i" (intrinsic safety) |  |  |
| 6.1 | Application This clause contains additional requirements for the repair, overhaul, reclamation and modification of equipment with type of protection "i". It shall be read in conjunction with Clause 4, which contains general requirements, and any other appropriate clauses if relevant. The relevant equipment standards which shall be referred to when repairing or overhauling an item of Ex "i" equipment are those to which the equipment was originally manufactured. NOTE Intrinsically safe equipment may have one of three levels of protection, Exia, Exib and Exic. However, the requirements for repair and overhaul apply to all levels of protection regardless of the hazardous area (i.e. zone 0, zone 1 or zone 2), in which the equipment is installed. Furthermore, the safety of intrinsically safe systems depends upon all pieces of equipment of which they are formed, and upon the interconnecting wiring. The same consideration should be given to those parts of the system which are installed in the non-hazardous area and in the hazardous area. |  |  |
| 6.2 | Repair and overhaul |  |  |
| 6.2.1 | Enclosures Enclosures of intrinsically safe equipment and associated apparatus are only required where intrinsic safety is dependent upon them. They are, however, often required for other reasons. Therefore, if the equipment has an enclosure, repair and overhaul activities should not reduce the protection offered by the enclosure (i.e. its IP rating). |  |  |
| 6.2.2 | Cable entries Special entries are used to maintain the degree of ingress protection of the enclosure. Any repairs shall not result in reduction in the degree of ingress protection. |  |  |
| 6.2.3 | Terminations When refurbishing terminal compartments, any terminals replaced shall normally be of the same type that they replace. Where the same type is not available, any alternative type used shall satisfy the creepage (according to CTI) and clearance requirements specified in the standard for the maximum voltage of the equipment and the separation required by the standard to avoid inadvertent cross-connection. |  |  |
| 6.2.4 | Soldered connections When it is necessary to carry out repairs which require soldering techniques to be used, care shall be taken to ensure that the basis of certification is not invalidated; e.g., – different requirements of redundancy apply to the connection depending on whether machine or hand soldering is used; – different requirements for creepage distances apply dependent on whether the soldered joint is sweated and coated or not. |  |  |
| 6.2.5 | Fuses Fuses shall normally be replaced in any circumstance either with a replacement of identical type or, if this is not possible, with an alternative which has – the same rating or less; – the same prospective current rating or more at the same or greater voltage; – the same type of construction; – the same physical size. |  |  |
| 6.2.5 Cont. | Different fuse Where this is not possible, an evaluation of the effects of the chosen fuse on intrinsic safety shall be carried out by a person fully cognizant with the requirements of the standard to which the equipment was originally manufactured and shall be fully documented. |  |  |
| 6.2.6 | Relays If a relay is faulty, it shall be replaced by one which is identical. |  |  |
| 6.2.7 | Shunt diode safety barriers These devices are totally encapsulated and no repair shall be attempted. Where a barrier device is replaced, the replacement shall always have the same safety description and the value chosen for Um shall be equal to, or greater than, the Um of the original barrier. Care shall also be taken that differing physical construction does not destroy the 50 mm separation required between the intrinsically safe circuits and non-intrinsically safe circuits. |  |  |
| 6.2.8 | Printed circuit boards These parts of the equipment often have critical distances between conducting tracks (creepage distances) which shall not be reduced. Therefore, when components are replaced, care shall be taken in positioning them on the board. Where varnish is damaged during repair, insulating varnish of the type prescribed by the manufacturer shall be applied in the approved manner, for example, one coat if using dipping, two coats using other methods. |  |  |
| 6.2.9 | Optocouplers Only components of the same or directly equivalent type and certification shall be used as replacements. |  |  |
| 6.2.10 | Electrical components When replacing components such as resistors, transistors, zener diodes, etc., these may normally be replaced with items purchased from any source which are identical replacements. In exceptional circumstances, however, some manufacturers use a "select on test" procedure for some components. Where this is done, the documentation supplied with the equipment shall indicate that either replacements be obtained from the equipment manufacturer or selected by the method he recommends. |  |  |
| 6.2.11 | Batteries Only those types specified in the equipment manufacturer's instructions shall be used as replacements. Where batteries are encapsulated, the whole assembly shall be replaced. |  |  |
| 6.2.12 | Internal wiring Certain distances between conductors and their segregation are critical. Therefore, if disturbed, internal wiring shall be re-located in its original position. If insulation, screens, outer sheaths, and/or double insulation of wiring or the method of fixing are damaged, theyshall be replaced by equivalent material and/or re-fixed in the same configuration. |  |  |
| 6.2.13 | Transformers If a transformer is found to be faulty, the replacement shall be obtained from the equipment manufacturer. No attempt shall be made to repair or replace any embedded (encapsulated) thermal trip device. |  |  |
| 6.2.14 | Encapsulated components Encapsulated components, for example, batteries with internal current-limiting resistors or fuse-zener diode assemblies, are non-repairable and shall be replaced only with assemblies of the original design from the equipment manufacturer. |  |  |
| 6.2.15 | Non-electrical parts Where the equipment has non-electrical parts, for example, fittings or window, that do not affect the electrical circuit or creepage and clearance distances and hence the intrinsic safety, these parts may be replaced by new parts of equivalent type. |  |  |
| 6.2.16 | Testing Before equipment containing intrinsically safe circuits only is re-installed in the hazardous area, then after completion of the repair or overhaul the insulation between the intrinsically safe circuit and the enclosure shall be checked by applying a 500 V a.c. to 50 Hz to 60 Hz voltage between the terminals and the enclosure for 1 min. This test can be omitted if the enclosure is of insulating material or if one side of the circuit is galvanically connected to the enclosure for safety reasons. |  |  |
| 6.3 | Reclamation No attempt shall be made to reclaim components on which intrinsic safety depends. |  |  |
| 6.4 | Modifications Modifications which may affect the intrinsic safety of the equipment shall not be carried out without reference to the manufacturer and/or the certification authority. After modification, the equipment shall be assessed to ensure that it complies with the intrinsically safe system documentation before it is returned to service. It is recommended that this assessment be carried out by a person other than the one who carried out the modification. |  |  |
| 7 | Additional requirements for the repair and overhaul of equipment with type of protection "p" (pressurized) |  |  |
| 7.1 | Application This clause contains additional requirements for the repair, overhaul, reclamation and modification of equipment with type of protection "p". It shall be read in conjunction with Clause 4, which contains general requirements, and any other appropriate clauses if relevant. The relevant equipment standards which shall be referred to when repairing or overhauling an Ex "p" equipment are those to which the equipment was originally manufactured (see IEC 60079-2). |  |  |
| 7.2 | Repair and overhaul |  |  |
| 7.2.1 | Enclosures While it is preferable to obtain new parts from the manufacturer, in principle a damaged part may be repaired or replaced with another given that, when compared with the original, it – is of at least equivalent strength; – does not result in a greater leakage rate of protective gas; – does not restrict the flow of protective gas into or through the enclosure; – is not shaped or fitted so as to permit the explosive atmosphere to enter the enclosure; – is not of a construction which would result in stagnant volumes of atmosphere inside the enclosure; – does not reduce the rate of heat dissipation from the enclosure or its content, so that it no longer complies with its temperature class. |  |  |
| 7.2.1. Cont. | Gaskets or other sealing devices shall be replaced with others of the same material. However, a different gasket material may be used provided that it is suitable for its purpose and is compatible with the environment. |  |  |
| 7.2.2 | Cable and conduit entries Entries shall preserve the degree of ingress protection originally provided and shall not allow increased leakage of pressurizing gas. |  |  |
| 7.2.3 | Terminations The preservation of creepage and clearance distances as originally provided shall be ensured. |  |  |
| 7.2.4 | Insulation Any replacement insulation used in the course of repair or overhaul shall be at least of the quality and class of that originally employed (see IEC 60085). |  |  |
| 7.2.5 | Internal connections Internal connections shall not be electrically, thermally or mechanically inferior to those originally fitted and shall be of a standard at least equivalent to that of the original design. |  |  |
| 7.2.6 | Windings |  |  |
| 7.2.6.1 | General The original winding data shall preferably be obtained from the manufacturer. If this is not possible, then use may be made of copy winding techniques. The materials used in rewinding shall comprise an appropriate insulation system. If superior insulation is proposed compared to that of the original, the rating of the winding shall not be increased without reference to the manufacturer, as the temperature classification of the equipment could then be adversely affected. |  |  |
| 7.2.6.2 | Repair of rotating machine rotors Faulty die-cast aluminium rotor cages shall be replaced by new rotors obtained from the manufacturer or his distributor. Bar-wound cage rotors shall be rewound using materials of similar or improved specification. Particular care is necessary to ensure that, when replacing conductors in a cage rotor, such conductors are tight in the slots. The method of achieving tightness employed by the manufacturer shall be adopted. |  |  |
| 7.2.6.3 | Testing after repair of windings |  |  |
| 7.2.6.3.1 | General Windings, after complete or partial repair, shall be subjected, with the equipment assembled, to the following tests, as far as reasonably practicable. |  |  |
| 7.2.6.3.1 | a) Winding resistance test The resistance of each winding shall be measured at room temperature and verified. In the case of three-phase windings, the resistance of each phase or between line terminals shall be balanced as far as is reasonable, unbalance of less than 5 % of middle value being acceptable. |  |  |
| 7.2.6.3.1 Cont. | b) Insulation resistance test An insulation resistance test shall be applied to measure the resistance between the windings and earth, between windings where possible, between windings and auxiliaries, and between auxiliaries and earth. A minimum test voltage of 500 V d.c. is recommended. Minimum acceptable insulation resistance values are a function of rated voltage, temperature, type of equipment and whether the rewind is partial or complete NOTE The insulation resistanceshould not be less than 20 MΩ at 20 °C on a completely rewound equipment intended for use up to 690 V. |  |  |
| 7.2.6.3.1 | c) High voltage test A high-voltage test, in accordance with a relevant equipment standard, shall be applied between windings and earth, between windings where possible, and between windings and auxiliaries attached to the windings. |  |  |
| 7.2.6.3.1 Cont. | d) Rated voltage test The transformer or similar equipment shall preferably be energized at rated supply voltage. The supply current, secondary voltage and current shall be measured. The measured value shall be compared with that derived from the manufacturer's data, where available, and in three-phase systems shall be balanced in all phases, as far as is reasonable. |  |  |
| 7.2.6.3.1 Cont. | - High voltage equipment High-voltage (for example, 1 000 V a.c./1 500 V d.c. and above) and other special equipment may require additional tests. This shall be the subject of the repair or overhaul contract. |  |  |
| 7.2.6.3.2 | Rotating machines Rotating machines, in addition to the above tests, shall be subjected to the following tests, as far as is reasonably practicable. |  |  |
| 7.2.6.3.2 Cont. | - No load run The machine shall be run at full speed and the cause of any untoward noise and/or mechanical vibration investigated and corrected. |  |  |
| 7.2.6.3.2 Cont. | - Locked rotor test The stator windings of cage machines shall be energized at an appropriate reduced voltage, with the rotor locked, to obtain between 75 % and 125 % of full-load current and to ensure balance on all phases. (The test, which in some respects is an alternative to a full-load test, is used to confirm the integrity of the stator winding and its joints and to indicate the presence of rotor defects.) Unbalance of less than 5 % of the middle value is acceptable. |  |  |
| 7.2.6.3.2 Cont | - High voltage equipment High-voltage (for example, 1 000 V a.c./1 500 V d.c. and above) and non-cage machines may require alternative and/or additional tests. This shall be the subject of the repair or overhaul contract. NOTE Guidance on test voltages and additional tests for rotating machines is given in IEC 60034. |  |  |
| 7.2.7 | Light-transmitting parts Light-transmitting parts made from plastics shall not be cleaned with solvent. Household detergents are recommended for this purpose. |  |  |
| 7.2.8 | Encapsulated parts In general, encapsulated parts (for example, switching devices in luminaires) are not considered suitable for repair. |  |  |
| 7.2.9 | Batteries Where batteries are used, the manufacturer's advice shall be followed. |  |  |
| 7.2.10 | Lamps Lamp types specified by the manufacturer shall be used as replacements and the maximum wattage specified shall not be exceeded. |  |  |
| 7.2.11 | Lampholders Replacements listed by the manufacturer shall be used. |  |  |
| 7.2.12 | Ballasts Chokes or capacitors shall be replaced only by manufacturer's listed parts, unless reference is made to the manufacturer to determine if alternatives may be used. |  |  |
| 7.3 | Reclamation Reclamation using the techniques detailed in Clause 4 may be used with type of protection "p" equipment subject to the following restrictions of this clause. |  |  |
| 7.3.1 | Enclosures |  |  |
| 7.3.1.1 | General If damage to enclosures, terminal boxes and covers is to be repaired by welding or metal stitching, care shall be taken to ensure that the integrity of the equipment is not significantly impaired so as to degrade the type of protection, in particular, that it remains capable of withstanding the impact test and the appropriate level of overpressure. |  |  |
| 7.3.1.2 | Joints If damaged or corroded joint faces are to be machined, the mechanical strength and operation of the component shall not be impaired nor the degree of ingress protection affected. |  |  |
| 7.3.1.2 Cont. | Spigoted/cylindrical joints Spigoted joints are normally provided to achieve close tolerance location. Thus, machining the male part will require addition of metal to, and the machining of, the female part (or vice versa) to retain the location properties of the joint. If only one part is damaged, that part may be restored to its original dimensions by the addition of metal and re-machining. The addition of metal shall be by electroplating, sleeving or welding but metal spraying techniques which have a bond strength less than 40 MPa are not recommended. |  |  |
| 7.3.2 | Shafts and housings If shafts and bearing housings are to be reclaimed, this shall be carried out by the use of metal spraying or sleeving techniques. Welding may be appropriate with due regard to the limitations of this technique (see 4.4.2.4.5). |  |  |
| 7.3.3 | Sleeve bearings Sleeve-bearing surfaces may be reclaimed by electroplating, metal spraying or welding (except MMA) techniques. |  |  |
| 7.3.4 | Rotors and stators If rotors and stators are to be lightly skimmed to remove eccentricities and surface damage after consultation with the manufacturer, the resultant increased air gap between rotor and stator shall not produce higher external surface temperatures that infringe the temperature class of the machine. |  |  |
| 7.3.4. Cont | Core flux test Skimmed or damaged stator cores shall be subjected to a "flux test" to ensure that there are no remaining hot spots which could infringe the temperature classification or cause subsequent damage to the stator windings. |  |  |
| 7.4 | Modifications |  |  |
| 7.4.1 | Enclosures Enclosures not containing a source of release of flammable gas may be modified. Any modified part shall meet the conditions given in 7.2. Enclosures with an internal source of release of flammable gas such as analysers, chromatographs, etc. shall not be modified in any way whatsoever without reference to the manufacturer. The point(s) at which the level of overpressure and the rate of flow or purging gas is (are) monitored shall not be altered nor should the setting of any timer or other monitoring devices be changed. |  |  |
| 7.4.2 | Cable and conduit entries Special care shall be taken to ensure that if alteration is made to entries, the specified type of protection and degree of ingress protection are maintained. |  |  |
| 7.4.3 | Terminations Modification of terminations shall be made using good engineering practices. |  |  |
| 7.4.4 | Windings Voltage change Rewinding of the equipment for another voltage shall be carried out only after reference to the manufacturer provided that, for example, the magnetic loading, current densities and losses are not increased, appropriate new creepage and clearance distances are observed and the new voltage is within the limits of the certification documents. The rating plate shall be changed to show the new parameters. |  |  |
| 7.4.4. Cont. | Speed change Rewinding a rotating machine for a different speed shall not be carried out without reference to the manufacturer, since the electrical and thermal characteristics of the machine could be significantly altered to the point of being outside the limits imposed by the assigned temperature class if appropriate, and the efficacy of the pressurizing system could be jeopardized. |  |  |
| 7.4.5 | Auxiliary equipment In cases where additional auxiliary equipment is requested, for example, anti-condensation heaters or temperature sensors, the manufacturer shall be consulted to establish the feasibility of and the procedure for the proposed addition. |  |  |
| 8 | Additional requirements for the repair and overhaul of equipment with type of protection "e" (increased safety) |  |  |
| 8.1 | Application This clause contains additional requirements for the repair, overhaul, reclamation and modification of equipment with type of protection "e". It shall be read in conjunction with Clause 4, which contains general requirements, and any other appropriate clauses if relevant. The relevant equipment standards which shall be referred to when repairing or overhauling Ex "e" equipment are those to which the equipment was originally manufactured (see IEC 60079-7). |  |  |
| 8.2 | Repair and overhaul |  |  |
| 8.2.1 Para 1 | Replacement parts While it is preferable to obtain new parts from the manufacturer, in principle, damaged parts may be repaired or replaced with others, given that the degree of ingress protection and temperature classification as stipulated on the certification label are preserved. |  |  |
| 8.2.1 Para 2 | Ingress protection A more stringent degree of ingress protection than that specified in the equipment standard may have been provided to cater for environmental conditions in which case any repair shall not jeopardize such higher degree of ingress protection. |  |  |
| 8.2.1 Para 3 | Impact test Particular attention is drawn to impact test requirements of all parts of the enclosure and also the degree of ingress protection to be provided for air inlet and outlet openings, as given in the equipment standard. |  |  |
| 8.2.1 Para 4 | Clearances Adequate clearance shall be maintained between stationary and rotating parts in accordance with the equipment standard. Adequate clearance shall mean the clearance required by the manufacturer’s certified drawings or in the absence of drawings, minimum clearance as specified in IEC 60079-7. |  |  |
| 8.2.1 Para 5 | Surface finishes Attention is drawn to the effects of surface finishes, paint, etc. on the temperature classification of enclosures. Only finishes specified by the manufacturer shall be applied. Note from KAM; For installations in corrosive environments the original surface coating is often not adequate. More appropriate surface coatings should be discussed with the manufacturer, if possible, and customer |  |  |
| 8.2.1 Para 6 | Before returning to service Before a rewound or repaired rotating machine is put back into service, it is essential to ensure that any fan cover ventilation holes are not blocked or so damaged as to impair the passage of cooling air over the machine and that fan clearances are in compliance with the certification requirements. Should a fan or fan cover be so damaged as to require renewal, the replacement parts shall be obtained from the manufacturer. If unobtainable, they shall be of the same dimensions and at least of the same quality as the original parts. They shall, where appropriate, take account of the requirements of the equipment standard to avoid frictional sparking and electrostatic charging and of the chemical environment in which the machine is used. |  |  |
| 8.2.2 | Cable or conduit entries Entries shall preserve a minimum IP54 degree of ingress protection, in accordance with the requirements of IEC 60529, and at least the same IP rating as the equipment was originally designed for. |  |  |
| 8.2.3 Para 1 | Terminations The design of terminations in terms of the materials and construction used, the creepage and clearance distances and the comparative tracking indices of termination insulation will normally be fully specified in the certification documents. Replacement parts shall be obtained from the manufacturer or his advice sought regarding acceptable alternatives |  |  |
| 8.2.3 Para 2 | Loose leads Where terminations are loose leads, the methods of termination including insulation shall be in accordance with the certification documents. |  |  |
| 8.2.4 | Insulation Comprehensive details of the insulation system of windings, including the type of impregnation varnish, are normally included in the certification documents. Where this does not apply, full information shall be sought from the manufacturer. |  |  |
| 8.2.5 | Internal connections If internal connections are to be renewed, the insulation on such connections shall not be electrically, thermally or mechanically inferior to that originally supplied. |  |  |
| 8.2.5 Para 2 | Replacement connections The cross-sectional area of any replacement connection shall not be less than that originally fitted. The permitted methods of connecting conductors are given in the relevant standards. |  |  |
| 8.2.6 | Windings |  |  |
| 8.2.6.1 Para 1 | General The electrical construction of type of protection "e" equipment decisively influences the explosion safety and the repairer shall be in full possession of the necessary information and equipment. |  |  |
| 8.2.6.1 Para 2 | Failure to meet equipments std Unless the repairer can meet all the requirements of the equipment standard, rewinding shall be carried out by the original manufacturer. For HV windings, the additional requirements for insulation as defined in the equipment standard shall be followed. |  |  |
| 8.2.6.1 Para 3 | Rewind data Before the repair, the original winding data, which should generally be available from the manufacturer, should be obtained, i.e.: - type of winding – for example, single-layer, double-layer, etc.; - winding diagram; - number of conductors/slot, parallel paths per phase; - interphase connections; - conductor size; - insulation system, including varnish specification; - resistance/phase or between terminals. Where the original insulation system and/or varnish system is not available, the tE time shall be verified in accordance with the equipment standard. |  |  |
| 8.2.6.1 Para 4 | Copy winding Copy winding techniques are not permissible unless the tE time is verified in accordance with the equipment standard. The whole of the winding shall be restored to the original condition except that a partial winding replacement may be possible on larger equipment where this may be practicable, but only if reference has been made to the manufacturer or certifying authority. |  |  |
| 8.2.6.2 Para 1 | Repair of rotating machine rotors Rotors with faulty die-cast aluminium cages shall be replaced by completely new rotors obtained from the manufacturer or his distributor. |  |  |
| 8.2.6.2 Para 1 | Bar wound cage rotors Bar-wound cage rotors shall be rewound using materials of identical specifications. Particular care is necessary to ensure that if replacing conductors in a cage rotor such conductors are tight in the slots and that slots have not been damaged. The method of achieving tightness employed by the manufacturer shall be adopted. |  |  |
| 8.2.6.3 | Testing after repair of windings |  |  |
| 8.2.6.3.1 | General After complete or partial repair, windings shall be subjected, with the equipment assembled, to the following tests so far as is reasonably practicable. |  |  |
| 8.2.6.3.1 Cont. | - Winding resistance The resistance of each winding shall be measured at room temperature and verified. In the case of three-phase windings, the resistance of each phase or between line terminals should be balanced, as far as is reasonable, unbalance of less than 5 % of the middle value being acceptable |  |  |
| 8.2.6.3.1 Cont. | - Insulation resistance An insulation resistance test shall be applied to measure the resistance between the windings and earth, between windings where possible, between windings and auxiliaries, and between auxiliaries and earth. The minimum test voltage of 500 V d.c. is recommended. Minimum acceptable insulation resistance values are a function of rated voltage, temperature and type of equipment and whether the rewind is partial or complete. NOTE The insulation resistance should not be less than 20 M at 20°C on a completely rewound equipment intended for use up to 690 V. |  |  |
| 8.2.6.3.1 Cont. | - High voltage test A high-voltage test, in accordance with a relevant equipment standard, shall be applied between windings and earth, between windings where possible, and between windings and auxiliaries attached to the windings. |  |  |
| 8.2.6.3.1 Cont. | - Rated voltage test The transformer or similar equipment shall preferably be energized at rated supply voltage. The supply current, secondary voltage and current shall be measured. The measured value shall be compared with that derived from the manufacturer's data, where available, and in three-phase systems should be balanced in all phases, as far as is reasonable. |  |  |
| 8.2.6.3.1 Cont. | - High voltage equipment High-voltage (for example, 1 000 V a.c./1 500 V d.c. and above) and other special equipment may require additional tests. This shall be the subject of the repair or overhaul contract. |  |  |
| 8.2.6.3.2 | Rotating machines In addition to the above tests, rotating machines shall be subjected to the following tests so far as is reasonably practicable. |  |  |
| 8.2.6.3.2 Cont. | - No load test The machine shall be run at full speed and the cause of any untoward noise and/or mechanical vibration investigated and corrected. |  |  |
| 8.2.6.3.2 Cont. | - Locked rotor test The stator windings of cage machines shall be energized at an appropriate reduced voltage, with the rotor locked, to obtain between 75 % and 125 % of full-load current and to ensure balance on all phases. (The test, which in some respects is an alternative to a full load test, is used to confirm the integrity of the stator winding and its joints and to indicate the presence of rotor defects.) Unbalance of less than 5 % of the middle value is acceptable. |  |  |
| 8.2.6.3.2 Cont. | - High voltage machines High-voltage (for example, 1000 V a.c./1 500 V d.c. and above) and non-cage machines may require alternative and/or additional tests. This shall be the subject of the repair or overhaul contract. NOTE Guidance on test voltages and additional tests for rotating machines is given in IEC 60034. |  |  |
| 8.2.6.3.3 | Temperature sensors If temperature sensors are included to monitor winding temperatures, it is recommended that they are embedded in the winding before varnishing and curing. |  |  |
| 8.2.7 | Light-transmitting parts No attempt shall be made to repair light-transmitting parts and only replacement components provided by the manufacturer shall be used. Light-transmitting parts or other parts made of plastic shall not be cleaned with solvents. Household detergents may be used |  |  |
| 8.2.8 | Encapsulated parts In general, encapsulated parts (for example, switching devices in luminaires) are not considered suitable for repair or reclamation. |  |  |
| 8.2.9 | Batteries Where batteries are used, reference shall be made to the manufacturer's instructions before carrying out any repair or replacement. |  |  |
| 8.2.10 Para 1 | Lamps Lamp types specified by the manufacturer shall be used as replacements and the maximum wattage specified shall not be exceeded. |  |  |
| 8.2.10 Para 2 | Single pin florescent tubes Special care shall be taken with single-pin tubular fluorescent tubes. The single pin, when inserted in the lampholder, forms a flameproof enclosure and distortion or misalignment may affect the designed explosion protection. |  |  |
| 8.2.11 | Lampholders Only replacements specified by the manufacturer shall be used. In those cases where the wiring to the lampholder is factory-made (crimps, etc.), rewiring shall not be undertaken unless the repairer has the equipment to make up the wiring to the same standard. NOTE Lampholders for type of protection "e" luminaires are invariably of specific types, either single-pin for tubular fluorescent lamps or screw for other types. |  |  |
| 8.2.12 | Ballasts Defective chokes and capacitors shall only be replaced with the manufacturer's listed parts. |  |  |
| 8.3 | Reclamation Reclamation using the techniques detailed in Clause 4 may be used with the type of protection "e" equipment subject to the following restrictions of this clause. |  |  |
| 8.3.1 | Enclosures |  |  |
| 8.3.1.1 | General If minor damage to enclosures, terminal boxes and covers is to be repaired by welding or metal stitching, care shall be taken to ensure that the integrity of the equipment is not significantly impaired as to degrade the type of protection, in particular, that it remains capable of withstanding the impact test and maintains the degree of ingress protection. |  |  |
| 8.3.1.2 Para 1 | Joints If damaged or corroded joint faces are to be machined, the mechanical strength and operation of the component shall not be impaired nor the degree of ingress protection affected. |  |  |
| 8.3.1.2 Para 2 | Spigoted/cylindrical joints Where joints are provided to achieve close tolerance location, machining the male part may require addition of metal to it and also machining of the female part (or vice versa) to retain the location properties of the joint. If only one part is damaged, that part may be restored to its original dimensions by the addition of metal and re-machining. The addition of metal shall be by electroplating, sleeving or welding, but metal spraying techniques which have a bond strength less than 40 MPa is not recommended. |  |  |
| 8.3.1.3 | Shafts and housings If shafts and bearing housings are to be reclaimed, this may be carried out by use of metal spraying or sleeving techniques. Welding may be appropriate with due regard to the limitations of this technique (see 4.4.2.4.5). |  |  |
| 8.3.2 | Sleeve bearings Sleeve-bearing surfaces may be reclaimed by electroplating, metal spraying or welding (except MMA) techniques. |  |  |
| 8.3.3 Para 1 | Rotors and stators If rotors and stators are to be lightly skimmed to remove eccentricities and surface damage after consultation with the manufacturer, the resultant increased air gap between rotor and stator shall not produce - higher internal and/or external surface temperatures that infringe the temperature class of the machine, or - changes in electrical/mechanical performance which prevents the electrical/thermal protective device providing the tripping characteristics required to conform to the equipment standard. |  |  |
| 8.3.3 Para 2 | Core flux test Skimmed or damaged stator cores should be subjected to a “flux test” to ensure that there are no remaining hot spots which could infringe the temperature classification or cause subsequent damage to the stator windings. |  |  |
| 8.4 | Modifications |  |  |
| 8.4.1 | 8.4.1 Enclosures Enclosures may be modified provided that the specified temperature classification, degree of ingress protection and impact test requirements of the appropriate standards are met. |  |  |
| 8.4.3 | Terminations No modification of terminations shall be made without reference to the manufacturer. |  |  |
| 8.4.4 Para 1 | Voltage change Rewinding of the equipment for another voltage shall be carried out only after reference to the manufacturer and provided that, for example, the magnetic loading, current densities and losses are not increased, new appropriate creepage and clearance distances are observed, and the new voltage, tE time and IA/IN ratio are within the limits of the certification documents. The rating plate shall be changed to show the new parameters. |  |  |
| 8.4.4 Para 2 | Speed change Rewinding a rotating machine for a different speed shall not be carried out without reference to the manufacturer, since the electrical and thermal characteristics of the machine could be significantly altered to the point of being outside the limits of the certification documents. |  |  |
| 8.4.5 | Auxiliary equipment In cases where additional auxiliary equipment is requested, for example, anti-condensation heaters or temperature sensors, the manufacturer shall be consulted to establish the feasibility of and the procedure for the proposed modification. |  |  |
| 9 | Additional requirements for the repair and overhaul of equipment with type of protection "n" (non-sparking) |  |  |
| 9.1 | Application This clause contains additional requirements for the repair, overhaul, reclamation and modification of equipment with type of protection "n". It shall be read in conjunction with Clause 4, which contains general requirements, and any other appropriate clauses if relevant. The relevant equipment standards which shall be referred to when repairing or overhauling an Ex "n" equipment are those to which the equipment was originally manufactured (see IEC 60079-15). |  |  |
| 9.2 | Repair and overhaul |  |  |
| 9.2.1 Para 1 | Enclosures Whilst it is preferable to obtain new parts from the manufacturer, in principle, damaged parts may be repaired or replaced with others, given that the degree of ingress protection and temperature classification as stipulated on the certification label is preserved. |  |  |
| 9.2.1. Para 2 | Ingress protection A more stringent degree of ingress protection than that specified in the equipment standard may have been provided to cater for environmental conditions, in which case any repair shall not jeopardize such higher degree of ingress protection. |  |  |
| 9.2.1. Para 3 | Impact test Particular attention is drawn to the impact test requirements of all parts of the enclosure as given in the equipment standard. |  |  |
| 9.2.1. Para 4 | Clearances Adequate clearance shall be maintained between stationary and rotating parts in accordance with the equipment standard. |  |  |
| 9.2.1. Para 5 | Restricted breathing enclosures Restricted breathing enclosures depend for their explosion protection on gaskets and other means of sealing. Particular attention should be paid to the condition of the sealing arrangements to preserve the type of protection. |  |  |
| 9.2.1. Para 6 | Surface finish Attention is drawn to the effect of surface finish, paint, etc. on the temperature classification of enclosures. Only finishes specified by the manufacturer should be applied Note from KAM: For installations in corrosive environments the original surface coating is often not adequate. More appropriate surface coatings should be discussed with the manufacturer, if possible, and customer |  |  |
| 9.2.1. Para 7 | Before returning to service Before a rewound or repaired rotating machine is put back into service, it is essential to ensure that any fan cover ventilation holes are not blocked or so damaged as to impair the passage of cooling air over the machine and that fan clearances are in compliance with the certification requirements. Should a fan or fan cover be so damaged as to require renewal, the replacement parts shall be obtained from the manufacturer. If unobtainable then they shall be of the same dimensions and at least of the same quality as the original parts. They shall, where appropriate, take account of the requirement of the standard to avoid frictional sparking or electrostatic charging, and of the chemical environment in which the machine is used. |  |  |
| 9.2.2 | Cable and conduit entries Entries shall preserve a minimum IP54 degree of protection in accordance with the requirements of IEC 60529. |  |  |
| 9.2.3 Para 1 | Terminations Care shall be taken when refurbishing terminal compartments to maintain clearances and creepages in accordance with the equipment standard. Where non-metallic screws are used for fixing, only replacement screws of similar materials shall be used. |  |  |
| 9.2.3 Para 2 | Loose leads Where terminations are loose leads, the method of termination including insulation shall be in accordance with the certification documents. |  |  |
| 9.2.4 | Insulation A class of insulation the same as or superior to that originally provided shall be employed, for example, a winding insulated with class E material may be repaired using class F material (see IEC 60085). |  |  |
| 9.2.5 Para 1 | Internal connections If internal connections are to be renewed, the insulation on such connections shall not be electrically, thermally or mechanically inferior to that originally supplied. |  |  |
| 9.2.5 Para 2 | Replacement connections The cross-sectional area of any replacement connection shall not be less than that originally fitted. |  |  |
| 9.2.6 | Windings |  |  |
| 9.2.6.1 Para 1 | General Where rewinding is carried out, it is essential that the original winding data are determined and that the new winding conforms to the original. If superior insulation is proposed compared to that of the original, the rating of the winding shall not be increased without reference to the manufacturer, as the temperature classification of the equipment could then be adversely affected. |  |  |
| 9.2.6.1 Para 2 | Winding data The original winding data should preferably be obtained from the manufacturer. If this is not reasonably practicable then use may be made of copy winding techniques. |  |  |
| 9.2.6.1 Para 3 | Partial winding replacement It is not recommended to have a partial winding replacement, except on larger equipment where this may be practicable, unless reference has been made to the manufacturer or certifying authority. |  |  |
| 9.2.6.2 Para 1 | Repair of rotating machine rotors A faulty die-cast aluminium rotor shall be replaced by a complete new rotor obtained from the manufacturer or his distributor. |  |  |
| 9.2.6.2 Para 2 | Bar wound cage rotors Bar-wound cage rotors shall be rewound using materials of similar or improved specification. Particular care is necessary to ensure that if replacing conductors in a cage rotor, such conductors are tight in the slots. The method of achieving tightness employed by the manufacturer shall be adopted. |  |  |
| 9.2.6.3 | Testing after repair of windings |  |  |
| 9.2.6.3.1 | General Windings, after complete or partial repair, shall be subjected, with the equipment assembled, to the following tests as far as is reasonably practicable. |  |  |
| 9.2.6.3.1 Cont. | - Winding resistance test The resistance of each winding shall be measured at room temperature and verified. In the case of three-phase windings, the resistance of each phase or between line terminals shall be balanced, as far as is reasonable. Note from JSA This should include “unbalance of less than 5% of the middle value being acceptable. |  |  |
| 9.2.6.3.1 Cont. | - Insulation resistance test An insulation resistance test shall be applied to measure the resistance between the windings and earth, between windings where possible, between windings and auxiliaries, and between auxiliaries and earth. A minimum test voltage of 500 V d.c. is recommended. Minimum acceptable insulation resistance values are a function of rated voltage, temperature, type of equipment and whether the rewind is partial or complete. NOTE The insulation resistance should not be less than 20 Mat 20 °C, on a completely rewound equipment intended for use at up to 690 V. |  |  |
| 9.2.6.3.1 Cont. | - High voltage test A high-voltage test in accordance with a relevant equipment standard shall be applied between windings and earth, between windings where possible, and between windings and auxiliaries attached to the windings |  |  |
| 9.2.6.3.1 Cont. | - Rated voltage test The transformer or similar equipment shall preferably be energized at rated supply voltage. The supply current, secondary voltage and current shall be measured. The measured value should be compared with that derived from the manufacturer's data, where available, and in three-phase systems shall be balanced in all phases, as far as is reasonable. |  |  |
| 9.2.6.3.1 Cont. | - High voltage equipment High-voltage (for example, 1000 V a.c./1 500 V d.c. and above) and other special equipment may require additional tests. This shall be the subject of the repair and overhaul contract. |  |  |
| 9.2.6.3.2 | Rotating machines Rotating machines, in addition to the above tests, shall be subjected to the following tests so far as is reasonably practicable. |  |  |
| 9.2.6.3.2. Cont | - No load test The machine shall be run at full speed and the cause of any untoward noise and/or mechanical vibration investigated and corrected. |  |  |
| 9.2.6.3.2. Cont | - Locked rotor test The stator windings of cage machines shall be energized at an appropriate reduced voltage, with the rotor locked, to obtain between 75 % and 125 % of full-load rated current and to ensure balance on all phases. (The test, which, in some respects, is an alternative to a full-load test, is used to confirm the integrity of the stator winding and its joints and to indicate the presence of rotor defects.) Note from JSA This should include “unbalance of less than 5% of the middle value being acceptable. |  |  |
| 9.2.6.3.2. Cont | - High voltage equipment High-voltage (for example 1000 V a.c./1 500 V d.c. and above) and non-cage machines may require alternative and/or additional tests. This shall be the subject of the repair or overhaul contract. NOTE Guidance on test voltage and additional tests for rotating machines is given in IEC 60034. |  |  |
| 9.2.6.4 | Temperature sensors If temperature sensors are included to monitor winding temperatures, it is recommended that they are embedded in the winding before varnishing and curing. |  |  |
| 9.2.7 | Light-transmitting parts Light-transmitting or other parts made of plastic shall not be cleaned with solvents. Household detergents may be used. |  |  |
| 9.2.8 | Encapsulated parts In general, encapsulated parts, for example, switching devices in luminaires, are not considered suitable for repair. |  |  |
| 9.2.9 | Batteries Where batteries are used, reference shall be made to the manufacturer's instructions before carrying out any repair or replacement. |  |  |
| 9.2.10 | Lamps Lamp types specified by the manufacturer shall be used as replacements and the maximum wattage specified shall not be exceeded. |  |  |
| 9.2.11 | Lamp holders Replacements listed by the manufacturer shall be used. |  |  |
| 9.2.12 | Ballasts Chokes or capacitors shall only be replaced with manufacturer's listed parts. If these are of proprietary manufacture, reference shall be made to the original manufacturer to determine if alternatives may be used. |  |  |
| 9.2.13 | Enclosed break devices In general, enclosed break devices are not considered to be suitable for repair. Replacement parts listed by the manufacturer shall be used. |  |  |
| 9.3 | Reclamation Reclamations using the techniques detailed in 4.4.2.4 may be used with type of protection "n" equipment subject to the following restrictions of this subclause. |  |  |
| 9.3.1 | Enclosures If minor damage to enclosures, terminal boxes and covers is to be repaired by welding or metal stitching, care shall be taken to ensure that the integrity of the equipment is not impaired, in particular, that it remains capable of withstanding the impact test and maintains the degree of ingress protection. |  |  |
| 9.3.2 Para 1 | Joints If damaged or corroded faces are to be machined, the mechanical strength and operation of the component shall not be impaired nor the degree of ingress protection affected |  |  |
| 9.3.2 Para 2 | Spigoted/cylindrical joints Spigoted joints are normally provided to achieve close tolerance location. Thus, machining the male part will require addition of metal to and machining of the female part (or vice versa) to retain the location properties of the joint. If only one part is damaged, that part may be restored to its original dimensions by the addition of metal and re-machining. The addition of metal shall be by electroplating, sleeving or welding, but metal spraying is not recommended. Note from JSA There is an error in the std. since metal spray with bond strength 40M Pa or greater is permitted in 5.3.1.2 b), 7.3.1.2 & 8.3.1.2 & should be permitted here. |  |  |
| 9.3.3. | Rotating machines |  |  |
| 9.3.3.1 | Shafts and housings Shafts and bearing housings may be reclaimed, preferably by use of metal spraying or sleeving techniques. Welding may be appropriate having due regard to the limitations of this technique (see 4.4.2.4). |  |  |
| 9.3.3.2 | Sleeve bearings Sleeve-bearing surfaces may be built up by electroplating, metal spraying or welding (except MMA) techniques. |  |  |
| 9.3.3.3 Para 1 | Rotors and stators If rotors and stators are to be lightly skimmed to remove eccentricities and surface damage, the resultant increased air gap between rotor and stator shall not produce higher internal or external surface temperatures that infringe the temperature class of the machine. |  |  |
| 9.3.3.3 Para 2 | Flux test Skimmed or damaged stator cores shall be subjected to a "flux test" to ensure that there are no remaining hot spots which could infringe the temperature classification or cause subsequent damage to the stator windings. |  |  |
| 9.4 | Modifications |  |  |
| 9.4.1 | Enclosures Enclosures may be modified provided that the specified temperature classification, degree of ingress protection and impact test requirements of the appropriate standard are met. |  |  |
| 9.4.2 | Cable and conduit entries Care shall be taken to ensure that the specified type of protection and degree of ingress protection are maintained. |  |  |
| 9.4.3 | Terminations Terminations shall be modified only if compliance with the equipment standard is maintained. |  |  |
| 9.4.4 Para 1 | Windings Voltage change It is permissible to rewind the equipment for another voltage after reference to the manufacturer provided that, for example, the magnetic loading, current densities and losses are not increased, appropriate new clearances and creepage distances are observed and the new voltage is within the limits of the certificate. The rating plate shall be changed to show the new parameters. |  |  |
| 9.4.4 Para 2 | Speed change Rewinding a rotating machine for a different speed is not permissible without reference to the manufacturer since the electrical and thermal characteristics of the machine could be significantly altered to the point of being outside the limits of the certification documents. |  |  |
| 9.4.5 | Auxiliary equipment In cases where additional auxiliary equipment is requested, for example, anti-condensation heaters or temperature sensors, the manufacturer shall be consulted to establish the feasibility of and procedure for the proposed modification. |  |  |
| 10 | Additional requirements for the repair and overhaul of equipment covered by IEC 60079-26 No repair or overhaul shall be carried out without availability of manufacturer information. In addition to meeting the requirements of IEC 60079-26, the applicable requirements of Clauses 5 to 8 of this standard still apply. If the certification documents are not available, the equipment shall be subjected to re-testing in accordance with the appropriate equipment standard. |  |  |
| 11 | Additional requirements for the repair and overhaul of equipment with type of protection ‘tD’ |  |  |
| 11.1 | Application This clause contains additional requirements for the repair, overhaul, reclamation and modification of equipment with type of protection "tD" (formerly known as DIP). It shall be read in conjunction with Clause 4, which contains general requirements, and any other appropriate clauses if relevant. The relevant equipment standards which shall be referred to when repairing or overhauling an Ex "tD" equipment are those to which the equipment was originally manufactured. NOTE The highest temperature which is attained by any part of the external surface of electrical equipment when tested under the defined dust-free or dust-layer conditions at the specified maximum ambient temperature (normally 40 °C) is marked on the equipment as a temperature value T. Practice A equipment with the zone prefixed "A" had been type-tested under dust-free conditions. Practice B equipment with the zone prefixed "B" had been type-tested under dust-layer conditions. |  |  |
| 11.2 | Repair and overhaul |  |  |
| 11.2.1 | Enclosures Whilst it is preferable to obtain new parts from the manufacturer, in principle, damaged parts may be repaired or replaced with others, given that the degree of ingress protection and temperature classification as stipulated on the certification label is preserved. |  |  |
| 11.2.1 Cont. | Visual inspection of seals If visual inspection (for example, ingress of dust or water) indicates that the effectiveness of sealing elements of the enclosure suffered from damage or ageing, such elements shall be replaced, preferably by using original spare parts supplied by the equipment manufacturer or by gasket parts of equivalent quality. |  |  |
| 11.2.1 Cont. | Signs of excess temperature If there are any signs that the specified temperature has been exceeded, or, in case of doubt, actual measurements according to IEC 61241-0 shall be made. If necessary, active parts such as windings, cores, cooling systems shall be replaced using manufacturer's spare parts and/or advice. |  |  |
| 11.2.1 Cont. | Ingress protection A more stringent degree of ingress protection than that specified in the equipment standard may have been provided to cater for environmental conditions, in which case any repair shall not jeopardize such higher degree of ingress protection. |  |  |
| 11.2.1 Cont. | Impact test Particular attention is drawn to the impact test requirements of all parts of the enclosure as given in the equipment standard. |  |  |
| 11.2.1 Cont. | Clearances Adequate clearance shall be maintained between stationary and rotating parts in accordance with the equipment standard. |  |  |
| 11.2.1 Cont. | Surface finish Attention is drawn to the effect of surface finish, paint, etc. on the temperature classification of enclosures. Only finishes specified by the manufacturer or equivalent should be applied. |  |  |
| 11.2.1 Cont. | Before returning to service Before a rewound or repaired rotating machine is put back into service, it is essential to ensure that any fan-cover ventilation holes are not blocked or so damaged as to impair the passage of cooling air over the machine and that fan clearances have minimum values as specified in IEC 61241-0, to avoid mechanical sparking. Should a fan, fan-cowl or air-inlet screen be so damaged as to require renewal, the replacement parts shall be obtained from the manufacturer. If unobtainable, then they shall be of the same dimensions and at least of the same quality as the original parts. They shall, where appropriate, take account of the requirement of the standard to avoid frictional sparking or electrostatic charging and of the chemical environment in which the machine is used. |  |  |
| 11.2.1 Cont. | Plastic materials Plastic material for enclosures, parts of enclosures or parts of the external ventilation system of rotating electrical machines are designed so that the danger of ignition due to propagating brush discharges is avoided. Spare parts, in addition to dimensional compliance, shall have the electrostatic discharge properties as specified in IEC 61241-0. |  |  |
| 11.2.2 | Cable and conduit entries Entries shall preserve a minimum IP5X or IP6X degree of ingress protection as appropriate in accordance with the requirements of IEC 60529. |  |  |
| 11.2.3 | Insulation A superior class of insulation compared with that originally used does not permit an increase in equipment rating without reference to the manufacturer. |  |  |
| 11.2.4 | Internal connections The cross-sectional area of any replacement connection shall not be less than that originally fitted. |  |  |
| 11.2.5 | Windings |  |  |
| 11.2.5.1 | General Where rewinding is carried out, it is essential that the original winding data are determined and that the new winding conforms to the original. If superior insulation is proposed compared to that of the original, the rating of the winding shall not be increased without reference to the manufacturer, as the temperature classification of the equipment could then be adversely affected. |  |  |
| 11.2.5.1 Cont. | Winding data The original winding data should preferably be obtained from the manufacturer. If this is not reasonably practicable, then use may be made of copy winding techniques. |  |  |
| 11.2.5.1 Cont. | Partial repair It is not recommended to have a partial winding replacement, except on a larger equipment where this may be practicable, unless reference has been made to the manufacturer or certifying authority. |  |  |
| 11.2.5.2 | Testing after repair of windings |  |  |
| 11.2.5.2.1 | General Windings, after complete or partial repair, shall be subjected, with the equipment assembled, to the following tests as far as is reasonably practicable. |  |  |
| 11.2.5.2.1 Cont. | - Winding resistance test The resistance of each winding shall be measured at room temperature and verified. In the case of three-phase windings, the resistance of each phase or between line terminals shall be balanced, as far as is reasonable; unbalance less than 5 % of middle value is acceptable. |  |  |
| 11.2.5.2.1 Cont. | - Insulation resistance test An insulation resistance test shall be applied to measure the resistance between the windings and earth, between windings where possible, between windings and auxiliaries, and between auxiliaries and earth. A minimum test voltage of 500 V d.c. is recommended. Minimum acceptable insulation resistance values are a function of rated voltage, temperature, type of equipment and whether the rewind is partial or complete. NOTE The insulation resistance should not be less than 20 Mat 20 °C, on a completely rewound equipment intended for use at up to 690 V. |  |  |
| 11.2.5.2.1 Cont. | - High voltage test A high-voltage test in accordance with a relevant equipment standard shall be applied between windings and earth, between windings where possible, and between windings and auxiliaries attached to the windings. |  |  |
| 11.2.5.2.1 Cont. | - Rated voltage test The transformer or similar equipment shall preferably be energized at rated supply voltage. The supply current, secondary voltage and current shall be measured. The measured value should be compared with that derived from the manufacturer's data, where available, and in three-phase systems shall be balanced in all phases, as far as is reasonable. |  |  |
| 11.2.5.2.1 Cont. | - High voltage equipment High-voltage (for example, 1 000 V a.c./1 500 V d.c. and above) and other special equipment may require additional tests. This shall be the subject of the repair and overhaul contract. |  |  |
| 11.2.5.2.2 | Rotating machines Rotating machines, in addition to the above tests, shall be subjected to the following tests so far as is reasonably practicable. |  |  |
| 11.2.5.2.2 Cont. | - No load run The machine shall be run at full speed and the cause of any untoward noise and/or mechanical vibration investigated and corrected. |  |  |
| 11.2.5.2.2 Cont. | - Locked rotor test The stator windings of cage machines shall be energized at an appropriate reduced voltage, with the rotor locked, to obtain between 75 % and 125 % of full-load rated current and to ensure balance on all phases. (The test, which in some respects is an alternative to a full load test, is used to confirm the integrity of the stator winding and its joints and to indicate the presence of rotor defects.) Note from JSA This should include “unbalance of less than 5% of the middle value being acceptable. |  |  |
| 11.2.5.2.2 Cont. | - High voltage equipment High-voltage (for example, 1 000 V a.c./1 500 V d.c. and above) and non-cage machines may require alternative and/or additional tests. This shall be the subject of the repair or overhaul contract. NOTE Guidance on test voltage and additional tests for rotating machines is given in IEC 60034. |  |  |
| 11.2.6 | Temperature sensors If temperature sensors are included to monitor winding temperatures, it is recommended that they are embedded in the winding before varnishing and curing. |  |  |
| 11.2.7 | Light-transmitting parts Light-transmitting or other parts made of plastic shall not be cleaned with solvents. Household detergents may be used. |  |  |
| 11.2.8 | Lamps Lamp types specified by the manufacturer shall be used as replacements and the maximum wattage specified shall not be exceeded. |  |  |
| 11.3 | Reclamation Reclamations using the techniques detailed in 4.4.2.4 may be used with type of protection "tD" equipment subject to the following restrictions of this subclause. |  |  |
| 11.3.1 | Enclosures If minor damage to enclosures, terminal boxes and covers is to be repaired by welding or metal stitching, care shall be taken to ensure that the integrity of the equipment is not impaired, in particular, that it remains capable of withstanding the impact test and maintains the degree of ingress protection. |  |  |
| 11.3.2 | Joints If damaged or corroded faces are to be machined, the mechanical strength and operation of the component shall not be impaired nor the degree of ingress protection affected. |  |  |
| 11.3.2. Cont. | Spigoted/cylindrical joints Spigoted joints are normally provided to achieve close tolerance location. Thus, machining the male part will require addition of metal to, and machining of, the female part (or vice versa) to retain the location properties of the joint. If only one part is damaged, that part may be restored to its original dimensions by the addition of metal and re-machining. The addition of metal shall be by electroplating, sleeving or welding, but metal spraying techniques which have a bond strength less than 40 MPa is not recommended. |  |  |
| 11.3.3 | Rotating machines |  |  |
| 11.3.3.1 | Shafts and housings Shafts and bearing housings may be reclaimed, preferably by use of metal spraying or sleeving techniques. Welding (except MMA) may be appropriate having due regard to the limitations of this technique (see 4.4.2.4). |  |  |
| 11.3.3.2 | Sleeve bearings Sleeve-bearing surfaces may be built up by electroplating, metal spraying or welding (except MMA) techniques. |  |  |
| 11.3.3.3 | Rotors and stators If rotors and stators are to be lightly skimmed to remove eccentricities and surface damage, the resultant increased air gap between rotor and stator shall not produce higher external surface temperatures that infringe the temperature class of the machine. |  |  |
| 11.3.3.3 Cont. | Core flux test Skimmed or damaged stator cores shall be subjected to a "flux test" to ensure that there are no remaining hot spots which could infringe the temperature classification or cause subsequent damage to the stator windings. |  |  |
| 11.4 | Modifications |  |  |
| 11.4.1 | Enclosures Enclosures may be modified provided that the specified temperature classification, degree of ingress protection and impact test requirements of the appropriate standard are met. |  |  |
| 11.4.2 | Cable and conduit entries Care shall be taken to ensure that the specified type of protection and degree of ingress protection are maintained. |  |  |
| 11.4.3 | Windings Voltage change It is permissible to rewind the equipment for another voltage after reference to the manufacturer provided that, for example, the magnetic loading, current densities and losses are not increased, appropriate new clearances and creepage distances are observed and the new voltage is within the limits of the certificate. The rating plate shall be changed to show the new parameters. |  |  |
| 11.4.3 Cont. | Speed change Rewinding a rotating machine for a different speed is not permissible without reference to the manufacturer since the electrical and thermal characteristics of the machine could be significantly altered to the point of being outside the limits of the certification documents. |  |  |
| 11.4.4 | Auxiliary equipment In cases where additional auxiliary equipment is requested, for example, anti-condensation heaters or temperature sensors, the manufacturer shall be consulted to establish the feasibility of and procedure for the proposed modification. |  |  |
| 12 | Additional requirements for the repair and overhaul of equipment with type of protection pressurization “pD” |  |  |
| 12.1 | Application Equipment used within enclosures that are certified as complying with the requirements of IEC 61241-2 is generally unspecified with respect to that standard. Variations can therefore be made to include equipment without invalidating the certificate. However, there are general restrictions such as electrical performance and temperature rating that are taken into consideration if changes to internal equipment are made. NOTE In contrast to type of protection ”p” purging is not allowed with type of protection “pD”. Internal cleaning of the enclosure is necessary before the electrical supply can be connected as per IEC 61241-2. |  |  |
| 12.2 | Repair and overhaul The requirements for repair and overhaul are identical with those of protection “p” as specified in Clause 7. |  |  |
| 12.3 | Reclamation The requirements for reclamations are identical with those of protection “p” as specified in Clause 7. |  |  |
| 12.4 | Modifications The requirements for modifications are identical with those of protection “p” as specified in Clause 7. |  |  |
| Annex A (normative) | Identification of repaired equipment by marking |  |  |
| A.1 | Marking information Repaired and overhauled equipment shall be marked on the main part in a visible place. This marking shall be legible and durable taking into account all relevant environmental conditions. |  |  |
| A.1 Cont. | Repair marking The marking shall include – the relevant symbol (see Clause A.2 below); – the standard number "IEC 60079-19" or national equivalent; – the name of the repairer or his registered trade mark and workshop certification, if any; – the repairer's reference number relating to the repair; – the date of the overhaul/repair. The marking may be on a plate permanently attached to the repaired equipment. |  |  |
| A.1 Cont. | Subsequent repair marking In the event of subsequent repairs, the earlier repair/overhaul plate shall be removed, a record being made of all the markings on it. |  |  |
| A.1 Cont. | Previous repair plate R in triangle If an earlier plate has been removed and it had the triangular symbol as shown in A.2.2, then the symbol on subsequent plates should also be triangular unless the repairer restores the whole equipment to full conformity with the certification documents. |  |  |
| A.1 Cont. | Non compliant equipment Equipment which, after repair or overhaul, conforms neither to the certification documents nor to the explosion protection concept standard shall have all the marking details relating to the explosion protection concept standard removed with the agreement of the user. |  |  |
| A.2 | Symbols |  |  |
| A.2.1 | Repair to certification docs. In accordance with certification and/or manufacturer’s specification R This mark is to be used only when the repair or reclamation is in accordance with this standard and the repairer has sufficient evidence of full compliance with the certification documents and/or manufacturer’s specification. |  |  |
| A.2.2 | Repair to standard In accordance with standards but not the certification documents R This mark is to be used when either |  |  |
| A.2.2 Cont. | - Repair to standard The equipment is changed during repair or reclamation so that it still complies with the restrictions imposed by this standard and the explosion protection standards to which it was manufactured, but repairer has insufficient evidence of full compliance with the certification documents; or - Assessed to standard The standards to which the previously certified equipment was manufactured are not known, but the requirements of this standard and the current edition of the relevant explosion protection standards have been applied but repairer has insufficient evidence of full compliance with the certification documents. An assessment, by a person competent in assessing explosion protected equipment has been conducted to verify compliance with the relevant level of safety prior to release of the equipment by the repairer. In these situations the certification labels should not be removed. NOTE These marking are required for the benefit of subsequent repairers and the only difference between the markings is the method of compliance. |  |  |
| A.2.3 | Other situations Equipment which, after repair or reclamation, does not conform to A.2.1 or A.2.2 should have its original manufacturer’s certification label removed or altered to give a clear indication that the equipment is not certified, until a supplementary certificate is obtained to cover the repair or overhaul. If the equipment is returned to its owner before such supplementary certification is obtained the record described in 4.4.1.5 should indicate that the equipment is not in serviceable condition and is not to be used in a place where explosive atmosphere is likely to occur. |  |  |
| Annex B (normative) | Knowledge, skills and competencies of “Responsible Persons” and “Operatives” |  |  |
| B.1 | Scope This annex specifies the knowledge, skills and competencies of persons referred to in this standard. (Refer to OD 015 for guide on determining competence level) |  |  |
| B.2 | Knowledge and skills |  |  |
| B.2.1 | Responsible Persons “Responsible Persons" who are responsible for the processes involved in the overhaul, repair and reclamation of specific types of explosion protection of explosion protected equipment, shall possess, at least, the following: |  |  |
| B.2.1 Cont | Responsible person knowledge & skills - general understanding of relevant electrical and mechanical engineering at the craftsperson level or above; - practical understanding of explosion-protection principles and techniques; - understanding and ability to read and assess engineering drawings; - familiarity with measurement functions, including practical metrology skills, to measure known quantities; - working knowledge and understanding of relevant standards in the explosion protection field; - basic knowledge of quality assurance, including the principles of traceability of measurement and instrument calibration. Such persons shall confine their involvement to overhaul, repair and reclamation in the nominated areas of competence and not engage themselves in modifications of explosion protected equipment without expert guidance. |  |  |
| B.2.2 | Operatives Operatives shall possess, to the extent necessary to perform their tasks, the following: a) understanding of the general principles of types of protection and marking; b) understanding of those aspects of equipment design which affect the protection concept; c) understanding of certification and relevant parts of this standard; d) ability to identify replacement parts and components authorized by the manufacturer; e) familiarity with the particular techniques to be employed in repairs referred to in this standard. |  |  |
| B.3 | Competencies |  |  |
| B.3.1 | General Competencies shall apply to each of the explosion-protection techniques for which the person is involved. For example: it is possible for a person to be competent in the field of repair and overhaul of Ex’d’ motors only and not be fully competent in repair of Ex’d’ switchgear or Ex’e’ motors. In such cases, the repair facility management shall define this in their documentation system. (Refer to OD 015 for guide on determining competence level) |  |  |
| B.3.2 | Responsible persons Responsible persons shall be able to demonstrate their competency and provide evidence of attaining the knowledge and skill requirements specified in B.2.1 relevant to the types of protection and/or types of equipment involved. |  |  |
| B.3.3 | Operatives Operatives shall be able to demonstrate their competency and provide evidence of attaining the knowledge and skill requirements specified in B.2.2 relevant to the types of protection and/or types of equipment involved. They shall also be able to demonstrate their competency in the – use and availability of documentation specified in 4.4.1.5.1; – production of job reports to the user as specified in 4.4.1.5.2; - use and production of repair facility records as specified in 4.4.1.5.3. |  |  |
| B.4 | Assessment The competency of responsible persons and operatives shall be verified and attributed, at intervals in accordance with 4.4.1.3 and 4.4.2.3, on the basis of sufficient evidence that the person a) has the necessary skills required for the scope of work; b) can act competently across the specified range of activities; and c) has the relevant knowledge and understanding underpinning competency. Note from JSA Assessment of “Operatives” & “Responsible Persons” who are craftsmen/tradesmen should include verification of work conducted either on Ex equipment in the service facility or on Ex equipment artifacts in a simulated work environment. |  |  |
| Annex C (normative) | Requirements for measurements in flameproof equipment during overhaul, repair and reclamation (including guidance on tolerances) |  |  |
| C.1 | General Evidence has come to light that there have been instances where equipment passed the Ex d flame transmission test with the gaps set to the maximum specified by the manufacturer but failed the test when set to the larger gaps permitted by the Ex d standard. As such equipment has not necessarily been marked with an 'X' on the certificate, there is no way of knowing whether the equipment can be safely repaired to the values allowed by the standard or whether it needs to be repaired to the smaller gaps specified by the manufacturer. Therefore, in the absence of drawings showing the manufacturer's gaps, repairers should use the guidance given in Table C.1. NOTE Figure C.1 is equivalent to Table C.1. |  |  |
| Table C.1 | – Determination of maximum gap of reclaimed parts |  |  |
| Figure C.1 | – Determination of maximum gap of reclaimed parts |  |  |