INTERNATIONAL ELECTROTECHNICAL COMMISSION

IEC SCHEME FOR CERTIFICATION TO STANDARDS FOR ELECTRICAL EQUIPMENT FOR EXPLOSIVE ATMOSPHERES (IECEx SCHEME)

Title: ExTAG Draft Decision Sheet - Use of temperature coefficient for ambient temperatures above 40C

CIRCULATED TO: Ex Testing and Assessment Group (ExTAG)

Following on from the Budapest 2004 ExTAG Meeting, and in accordance with Item 10.7 of the ExTAG Budapest Meeting Minutes, ExTAG/48/RM, this draft Decision Sheet prepared by BASEEFA (2001), as a modified version of ExTAG/46/CD, is issued to ExTAG members for approval.

At the request of the ExTAG Chairman and Secretary, I would ask that you consider the attached draft Decision Sheet. Should you have any comments or objections to this draft being published as an ExTAG approved Decision Sheet please advise the IECEx Secretariat, details below, by no later than 16th April 2004.

# Secretariat contact: Christine.kane@iecex.com

| IECEx Secretariat C/- SAI Building 286 Sussex Street Sydney NSW 2000 Australia | Contact Details: E-mail: chris.agius@iecex.com http://www.iecex.com |
| --- | --- |

| Standard: #### IEC 60079-11 | Clause: 7.1 | Sheet No. |
| --- | --- | --- |
| Subject: Use of temperature coefficient for ambient temperatures above 40C Status of document: Proposal/draft | Key words: - Temperature coefficient - ambient temperature - zener diode | Decision of meeting Date: Originator of proposal: AU (This modified Version prepared by GB) TC/SC involved: SC31G |

Question:  Should the temperature coefficient be included in power rating calculations and in the determination of maximum output parameter “Uo”, at ambient temperature over 40°C?

Answer:  There are two distinct parts to the question which need to be treated separately:

- Power rating calculations which are dealt with by the 2nd paragraph of IEC 60079-11 Clause 7.1 which take into account the effect of the mounting conditions and the ambient temperature range. The clause does not require the ambient temperature range to be used in calculation of the actual power dissipation.

- Determination of maximum output parameter “Uo” which is dealt with by the final para. of IEC 60079-11 Clause 7.1 which specifically excludes the need for detailed testing and analysis of components. This paragraph makes it clear that there is no need to take into account effects such as voltage elevation due to rise in temperature. The example given in the paragraph shows “Uo” to be nominal zener voltage + tolerance only.

Therefore, the ambient temperature range is taken into account when establishing device rating but not for the maximum output parameter “Uo” or the actual power dissipation within the device.