INTERNATIONAL ELECTROTECHNICAL COMMISSION SCHEME

FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SCHEME)

Title: ExTAG Draft Decision Sheet – Galvanically separating components

Circulated to: Ex Testing and Assessment Group (ExTAG)

This draft Decision Sheet, prepared by BASEEFA, is issued for your consideration. Please submit comments by -

2nd August 2005 to ExTAG Secretary, Mr Michel Brenon, via Christine Kane

## Michel Brenon

#### Michel Brenon

ExTAG Secretary

| Address: Standards Australia Building 286 Sussex Street Sydney NSW 2000 Australia | IECEx Secretariat Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 e-mail: chris.agius@iecex.com http://www.iecex.com | ExTAG Secretary Mr Michel Brenon/LCIE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 e-mail michel.brenon@lcie.fr |
| --- | --- | --- |

DRAFT IECEx / ExTAG DECISION SHEET

Title: Draft ExTAG Decision Sheet – Galvanically separating components

| Standard: #### IEC 60079-11 | Clause: 8.8 | Sheet No. |
| --- | --- | --- |
| Subject: Galvanically separating components Status of document: # Draft | Key words: - Isolating component - Opto-coupler | Decision of meeting Date: Originator of proposal: Baseefa TC/SC involved: SC31G |

Question:  Under what conditions can opto-couplers be used to provide infallible separation between intrinsically safe circuits?

Answer:  Isolating components shall be considered to provide infallible separation of separate intrinsically safe circuits if the following conditions are satisfied:

- the rating of the device shall be according to 7.1 (with the exceptions given in that clause still being applicable and including opto-couplers) unless it can be shown that the circuits connected to these terminals cannot invalidate the infallible separation of the devices. Protective techniques such as those indicated in 2nd paragraph of 8.8 may be necessary to avoid exceeding the rating of the opto-coupler.

- the device shall comply with the dielectric strength requirements in accordance with 6.4.12.

The manufacturer's rated isolation voltage for the infallible separation of the component under test shall be not less than the test voltage required by 6.4.12.

Note:	This text is identical (apart from clause reference nos.) to the text of clause 8.8.3 of IEC 60079-11

Ed 5 CDV.