INTERNATIONAL ELECTROTECHNICAL COMMISSION SCHEME

FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SCHEME)

- Title: ExTAG Draft Decision Sheet – Clearances, creepage distances and separations

Circulated to: Ex Testing and Assessment Group (ExTAG)

##### INTRODUCTION

- This draft Decision Sheet prepared by Australian Bodies covers Clearances, creepage distances and separations - and is issued for discussion during the ExTAG Meeting, Shanghai, 5th September 2006.

#### Michel Brenon

ExTAG Secretary

| Address: Standards Australia Building 286 Sussex Street Sydney NSW 2000 Australia | IECEx Secretariat Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 e-mail: chris.agius@iecex.com http://www.iecex.com | ExTAG Secretary Mr Michel Brenon/LCIE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 e-mail michel.brenon@lcie.fr |
| --- | --- | --- |

- RECORD OF IECEx / ExTAG DECISIONS

| - Standard: - lEC 60079-11:1999-02 | - Clause: 6.4 | - Sheet No. 2005/ |
| --- | --- | --- |
| - Subject: - Clearances, creepage distances and separations - Status of document: draft | - Key words: - Creepage - Clearances - Separations | Decision of meeting Date: Originator of proposal: AU |
| Question. IEC 60079-11 does not include any separation distances or CTI values for voltage above 1,575 V. Table 4 note 1 states that there are no values proposed at present. It is also noted that the next draft edition does not include any values for separations above 1,575 V either. Until such time when this data is published what values should be used? Note: High Voltages such as 3.3kV are required for Earth Fault Lock Out systems for Group I applications and must be Intrinsically Safe according to AS2081, & it must connect to the 3.3kV phase conductors Answer. Until IEC 60079-11 provides values for separations and CTI above 1,575 V it is proposed that the following values are used. (The values are based on data for the clearance and creepages distances in air as listed in IEC 60079.7 and AS2380.7 data for creepage under coating) |  |  |

| 1 | Voltage |  | 10 | 30 | 60 | 90 | 190 | 375 | 550 | 750 | 1000 | 1300 | 1575 | 3300 | 4700 | 9500 | 15600 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | (peak value) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | V |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 | Clearance |  | 1.5 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 14 | 16 | 36 | 49 | 94 | 151 |
|  | mm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 | Separation distance through casting compound |  | 0.5 | 0.7 | 1 | 1.3 | 1.7 | 2 | 2.4 | 2.7 | 3.3 | 4.6 | 5.3 | 9 | 12 | 20 | 33 |
|  | mm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 | Separation distance through solid insulation |  | 0.5 | 0.5 | 0.5 | 0.7 | 0.8 | 1 | 1.2 | 1.4 | 1.7 | 2.3 | 2.7 | 4.5 | 6 | 10 | 16.5 |
|  | mm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 | Creepage distance in air |  | 1.5 | 2 | 3 | 4 | 8 | 10 | 15 | 18 | 25 | 36 | 49 | 67 | 86 | 160 | 245 |
|  | mm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 | Creepage distance under coating |  | 0.5 | 0.7 | 1 | 1.3 | 2.6 | 3.3 | 5 | 6 | 8.3 | 12 | 16.3 | 23 | 30 | 53 | 81 |
|  | mm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 | Comparative tracking index (CTI) | ia |  | 100 | 100 | 100 | 175 | 175 | 275 | 275 | 275 | 275 | 275 | 500 | 500 | 500 | 500 |
|  |  | ib |  | 100 | 100 | 100 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 500 | 500 | 500 | 500 |
| NOTE 1 – At voltages up to 10 V. the CTI of insulating materials is not required to be specified. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Notes

1.	The complete table has been included for completeness only. Proposed additions are shown in bold italized text.

2.	Row 6, 15600V column AS2380.7 listed 80 mm creepage under coating.

3.	A CTI value of 500 has been recommended this aligns with Material group II in IEC60079.7