ExTAG(Melbourne/UL)03

ExTAG/180/CD - Draft Decision Sheet - Ventilation of battery containers

UL comments are as follows: 

We concur that the third paragraph in clause 7.4.2 of IEC 60079-11: 2006 applies to battery containers of both primary and secondary battery types.  However, further clarification is needed on this clause with regard to the difference between a battery container and an individual sealed cell.  Note 3 of clause 7.4.2 implies that individual sealed cells should be tested in accordance with 10.5.4.  The need to apply this clause to an individual IEC 60086-1 type “L” cell is questionable, provided the cell complies with the electrolyte leakage test in clause 10.5.2 of IEC 60079-11: 2006.  A correlation between which sealed cells in Table 7 and 8 of IEC 60079-0: 2004 that pass the electrolyte leakage test and would still require testing in accordance 10.5.4 could be made. 

Alternately, it could be indicated that clause 10.5.4 only applies to battery containers.