INTERNATIONAL ELECTROTECHNICAL COMMISSION SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE

IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Circulated to: ExTAG – IECEx Testing and Assessment Group

TITLE: Draft Decision Sheet - A decision is required from the IECEx to confirm or negate the locked rotor test as a mandatory requirement in IEC 60079-19.

INTRODUCTION

Previously prepared draft decision sheet, ExTAG/196/CD has been revised in line with the decisions of the 2010 Berlin ExTAG meeting (including comments listed in ExTAG/204/CC) and is now issued as ExTAG/196A/CD for consideration during the 2011 Split ExTAG meeting.

## Michel Brenon

ExTAG Secretary

| Address: IECEx Secretariat 286 Sussex Street Sydney NSW 2000 Australia | Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 E-mail: chris.agius@iecex.com http://www.iecex.com | ExTAG Secretary Mr Michel Brenon/LCIE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 e-mail michel.brenon@lcie.fr |
| --- | --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: Standard IEC60079-19:2006 | Clauses: 5.2.6.3.2, 7.2.6.3.2, 8.2.6.3.2, 9.2.6.3.2 & 11.2.5.2.2 |  |
| --- | --- | --- |
| Subject: Locked rotor test for rewound rotating machines Status of document: Draft | Key words: Locked rotor test | # Date: Revised July 2011 Originator of proposal: GB |
| Question: Is it obligatory to conduct the locked rotor test given as item b) in the following clauses of IEC 60079-19:2006 5.2.6.3.2 7.2.6.3.2 8.2.6.3.2 9.2.6.3.2 11.2.5.2.2 Answer: No The lead-in to each clause uses the phrase “as far as reasonably practical”. The subsequent edition of the standard, IEC 60079-19:2011, emphasizes the optional nature of this test by introducing a note to the corresponding clause: “NOTE 2 Where this test is not reasonably practical other means of verification should be used.” It should be noted that it is not normally practical to conduct this test on larger motors, and that alternative tests such as surge testing, growler testing, impedance testing or other test agreed between the owner of the rotating machine and the service facility may be used to satisfy the requirement of the standard. The definition of “larger” will vary with the available test facilities and the mounting arrangement of the machine. It would be normal to conduct the test on foot mounted machines up to about 15 kW with an absolute maximum of about 200 kW for test facilities with appropriate safe means of locking the rotor. |  |  |