### ExTAG DS  2002/003

2002 10 21

RECORD OF IECEx / ExTAG DECISIONS

| Standard: IEC60079-11: 1999-02 Sheet No. 20021003 | Clause: 7.11, 7.4.8 | Sheet No. 2002/003 |
| --- | --- | --- |
| Subject: Rating of components for - Component rating Date: 2002-10-21 battery chargeable Originator of proposal: equipment Status of document: TC/SC involved: SC31G adopted | Key words: Component rating Battery chargeable | Decision of meeting Date: 2002-10-21 Originator of proposal: AU TC/SC involved: SC31G |
| Question: How does the connection of a battery charger to equipment affect the rating of components? Answer: When the equipment contains batteries, which need to be recharged, the components on which intrinsic safety depends shall comply with the requirements of IEC 60079-11:1999 Clause 7.1. This includes when the charger is connected to the equipment in the safe area and the internal battery may have been disconnected either due to a connection failure or battery high resistance. This is the requirement of Clause 7.4.8. Comment: In general this is likely to require components to have a higher rating than when the effect of the charger is ignore |