| Reference No: |  |  |  |  |  |  |  |  |  |  | #### IEC 61241-1-1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ## Field of application This form is intended to be used when assessing and testing electrical apparatus for explosive atmospheres according to the standard specified in the adjoining column. The test results are valid for the tested items only. Reproduction This report must not be reproduced other than in its entirety except with the prior written approval of the issuing body | Standard: # IEC 61241-1-1 : 1993 Electrical apparatus for use in the presence of combustible dust |  |  |  |  | ## Instructions for use The comment columns can be used to e.g. specify test values, applied alternative requirements/tests or to refer to enclosed additional pages with comments. Abbreviations: N/A = Not applicable (for the assessment/test of the equipment and its design documentation) The applicant is the body/person who has requested the assessment/test and to which the results, as specified in this report, are provided. The short descriptions in the column for "Clause" do not replace the complete text in the standard. |  |  |  |  |  |
|  | Amendments: None |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | # This test report may only be used for the # IECEx Scheme and must be accompanied by an ExTR cover page issued by an ExCB. |  |  |  |  |  |
| ## Product name |  |  |  |  | # Model/Type designation |  |  |  |  |  |  |
| Serial No | Code (e.g. DIP A21 TA ) |  |  |  |  |  | Ambient temperature [min-max] |  |  |  |  |
| Applicant [name and postal address] |  |  |  |  | Manufactured by [name and postal address] |  |  |  |  |  |  |
| Test sample received [date] |  |  |  |  |  |  |  |  |  |  |  |
| ## Product description |  |  |  |  |  |  |  |  |  |  |  |
| The equipment complies with the standard [yes/no] | ## Prepared by |  |  |  |  |  |  |  |  | Date [year-month-day] |  |
|  | [signature] |  |  |  |  |  |  |  |  |  |  |

Sheet 1 of 45

| Reference No: |  |  |  |  |  |  | #### IEC 61241-1-1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause |  | Results |  |  |  |  |  |  |
|  |  | Pass | Fail | N/A | Comments |  |  | ExCB Review |
| 1.1 | Scope |  |  |  |  |  |  |  |
| 1.2 | Normative References |  |  |  |  |  |  |  |
| 2 | Definitions |  |  |  |  |  |  |  |
| 3.1 | Construction (all electrical apparatus; application of and deviations from IEC79-0) |  |  |  |  |  |  |  |
| 3.2 | Supplementary (for electrical apparatus to Practice B for use in zone 21) |  |  |  |  |  |  |  |
| 3.2.1 | Joints |  |  |  |  |  |  |  |
| 3.2.2 | Operating rods, spindles or shafts |  |  |  |  |  |  |  |
| 3.2.3 | Clearance of bolts |  |  |  |  |  |  |  |
| 3.3 | Supplementary requirements for certain electrical apparatus. |  |  |  |  |  |  |  |
| 4.1 | General tests (application of and deviations from IEC 79-0) |  |  |  |  |  |  |  |
| 4.2 | Dust-tightness test |  |  |  |  |  |  |  |
| 4.2.1 | Dust-tight apparatus to Practice A |  |  |  |  |  |  |  |
| 4.2.2 | Dust-protected apparatus to Practice A |  |  |  |  |  |  |  |
| 4.2.3.1 | Heat cycling test (Practice B; dust-tight apparatus) |  |  |  |  |  |  |  |
| 4.2.3.2 | Acceptance criteria (Practice B; dust-tight apparatus) |  |  |  |  |  |  |  |
| 4.2.3.3 | Verification of joints (Practice B; dust-tight apparatus) |  |  |  |  |  |  |  |
| 4.2.4.1 | Heat cycling test (Practice B; dust-protected apparatus) |  |  |  |  |  |  |  |
| 4.2.4.2 | Acceptance criteria (Practice B; dust-protected apparatus) |  |  |  |  |  |  |  |
| 4.3.1 | Temperature measurement |  |  |  |  |  |  |  |
| 4.3.2 | Temperature control |  |  |  |  |  |  |  |
| 4.3.3 | Ambient temperature range |  |  |  |  |  |  |  |
| 4.3.4.1 | Dust free test (Practice A) |  |  |  |  |  |  |  |
| 4.3.4.2 | Maximum surface temperature of the enclosure (Practice A) |  |  |  |  |  |  |  |

Sheet 2 of 45

| Reference No: |  |  |  |  |  |  | #### IEC 61241-1-1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause |  | Results |  |  |  |  |  |  |
|  |  | Pass | Fail | N/A | Comments |  |  | ExCB Review |
| 4.3.5.1 | Dust-blanket test (Practice B) |  |  |  |  |  |  |  |
| 4.3.5.2 | Maximum surface temperature of the enclosure (Practice B) |  |  |  |  |  |  |  |
| 5.1 | Marking (General) |  |  |  |  |  |  |  |
| 5.2.1 | Marking of all electrical apparatus |  |  |  |  |  |  |  |
| 5.2.1.1 | Supplementary marking (Practice A for zone 21) |  |  |  |  |  |  |  |
| 5.2.2 | Supplementary marking (Practice A for zone 22) |  |  |  |  |  |  |  |
| 5.2.3.1 | Supplementary marking (Practice B for zone 21) |  |  |  |  |  |  |  |
| 5.2.3.2 | Supplementary marking (Practice B for zone 22) |  |  |  |  |  |  |  |

Sheet 3 of 45

| Section 2 EVALUATION RECORD To be completed by ExTL IEC 61241-1-1:1993 Electrical apparatus for use in the presence of combustible dust |  |
| --- | --- |
| Report |  |
| Reference No. |  |
| Tested by ( + signature) Approved by (+ signature) Date of issue Content |  |
| This report is based on a standard format prepared by CSA International |  |
| Client |  |
| Name Address |  |
| Evaluation Record Form No. ExTR6124111/Version 1a/DS Copyright reserved to the bodies participating in the IECEx Scheme |  |
| Testing laboratory |  |
| Name Address Testing location |  |
| Test item Standard IEC 61241-1-1 Description. Trademark. Model and/or type reference Manufacturer |  |

Sheet 4 of 45

| Test Item (continued) Rating(s) Type of transformers (where relevant) Application Protection index Other characteristics Rated ambient temperature ta (OC) | stationary / portable / hand-held IP |
| --- | --- |
| Other information |  |

Sheet 5 of 45

General remarks This evaluation record is not valid unless appended to an IECEx Test Report issued by an ExCB, in accordance with IECEx 02. This evaluation record shall not be reproduced except in full without the written approval of the testing laboratory. The test results presented in this evaluation record relate only to the item tested.

Copy of marking plate

Sheet 6 of 45

| MANUFACTURER'S DOCUMENTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Subject | Drawing No. | Rev. | Date |

Sheet 7 of 45

Evaluation Record

| IEC 61241-1-1 |  | SECTION 1 : SPECIFICATION FOR APPARATUS 1/2 | # APPLIED |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CLAUSE |  | REQUIREMENTS | YES | NO | ENCL. |  |  |
| 1 |  | General |  |  |  |  |  |
| ### Apparatus: |  |  |  |  |  |  |  |
| ### Scope |  |  |  |  |  |  |  |
| The electrical apparatus defined above is feasible for coverage for use in areas where combustible dust may be present in quantities which could lead to a fire or explosion hazard. |  |  |  |  |  |  |  |
|  | YES |  |  |  |  |  |  |
|  | NO |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |
| Form sheets included for apparatus covered in this report: |  |  |  |  |  |  |  |
|  | Attachment A – apparatus for use in zone 21 |  |  |  |  |  |  |
|  | Attachment B – apparatus for use in zone 22 |  |  |  |  |  |  |
| Overview: |  |  |  |  |  |  |  |
| Normative references |  |  |  |  |  |  |  |
| The electrical apparatus has been assessed to the most recent editions of the standards which are referenced and posted as provisions of this part of IEC 60079: |  |  |  |  |  |  |  |
|  | YES |  |  |  |  |  |  |
|  | NO |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |

Sheet 8 of 45	(IEC 61241-1-1, 1993)

| IEC 61241-1-1 |  |  |  | SECTION 1 : SPECIFICATION FOR APPARATUS 2/2 |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ##### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  | YES |  | NO |  | ENCL. |  |  |  |  |
| 2 |  |  |  | Definitions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.1 |  |  |  | ## Requirements for all electrical apparatus |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.2 |  |  |  | ## Supplementary requirements to practice B, zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.3 |  |  |  | ## Supplementary requirements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Definitions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | All definitions covered in Clause 2 apply, as noted for the specific requirements herein |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Requirements for all electrical apparatus |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Application of and deviations from IEC 60079-0: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | apparatus for use in zone 21 – ref. Attachment A |  |  |  |  |  |  |  |  |  |  |  | apparatus for use in zone 22 – ref. Attachment B |  |  |  |  |  |  |  |  |  |  |  |  |
| Supplementary requirements for electrical apparatus to practice B for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Joints: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | plain joint; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | minimum contact width of the plain joint |  |  |  |  |  |  |  |  |  |  | 5 mm |  |  |  | 22 mm |  |  |  |  |  |  |  |  |  |
|  | maximum allowable clearance |  |  |  |  |  |  |  |  |  |  | 0.05 mm |  |  |  | 0.22 mm |  |  |  |  |  |  |  |  |  |
|  | spigotted joint; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | having axial and radial paths neither of which < 1.2mm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | L (mm) |  |  | W (mm) |  |  |
|  | minimum contact width of axial (L) + radial (W) |  |  |  |  |  |  |  |  |  |  | 5 mm |  |  |  | 22mm |  |  |  |  |  |  |  |  |  |
|  | maximum diametrical and radial section clearances |  |  |  |  |  |  |  |  |  |  | 0.05 mm |  |  |  | 0.22 mm |  |  |  |  |  |  |  |  |  |
|  | gasketed joint; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | maximum opening dimension |  |  |  |  |  |  |  |  |  |  | 305 mm |  |  | 915 mm |  |  | > 915 mm |  |  |  |  |  |  |  |
|  | minimum required effective width of gasketed joint |  |  |  |  |  |  |  |  |  |  | 3 mm |  |  | 4.8 mm |  |  | 9.5 mm |  |  |  |  |  |  |  |
| Operating rods, spindles and shafts: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | running contact seal(s) ( |  |  |  |  |  |  | not depended upon to ensure dust-tightness) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | power shaft(s) |  |  |  |  |  | operating rod(s) |  |  |  |  |  |  | spindle(s) |  |  |  |  |  |  |  |  |  |  |  |
|  | minimum length of path for power spindles |  |  |  |  |  |  |  |  |  |  | 12.5 mm |  |  |  | 38.5 mm |  |  |  |  |  |  |  |  |  |
|  | maximum allowable diametrical clearance |  |  |  |  |  |  |  |  |  |  | 0.26 mm |  |  |  | 0.57 mm |  |  |  |  |  |  |  |  |  |
|  | minimum length of path for operating rods, spindles or shafts |  |  |  |  |  |  |  |  |  |  | 12.5 mm |  |  |  | 25.5 mm |  |  |  |  |  |  |  |  |  |
|  | maximum allowable diametrical clearance |  |  |  |  |  |  |  |  |  |  | 0.13 mm |  |  |  | 0.21 mm |  |  |  |  |  |  |  |  |  |
| Clearance of bolts: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | maximum diametrical clearance, |  |  |  |  |  |  |  |  | mm Clearance  0.26 mm Path length  12.5 mm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Supplementary requirements for certain electrical apparatus |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Application of and deviations from IEC 60079-0: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | apparatus for use in zone 21 – ref. Attachment A |  |  |  |  |  |  |  |  |  |  |  | apparatus for use in zone 22 – ref. Attachment B |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 9 of 45 	(IEC 61241-1-1, 1993)

| ###### IEC 61241-1-1 |  |  |  |  | VERIFICATION AND TESTS 1/2 |  |  |  |  |  |  |  |  | # APPLIED |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  | YES | NO | ENCL. |  |
| 4.1 |  |  |  |  | General tests |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.2 |  |  |  |  | Dust-tightness test |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General tests |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Application of and deviations from IEC 60079-0: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | apparatus for use in zone 21 – ref. Attachment A |  |  |  |  |  |  |  |  |  |  |  | apparatus for use in zone 22 – ref. Attachment B |  |  |  |  |
| Dust-tightness tests |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Dust-tight apparatus to Practice A |  |  |  |  |  |  |  |  | (requirements of IEC 60529 for IP6X) |  |  |  |  |  |  |  |
|  | Dust-protected apparatus to Practice A |  |  |  |  |  |  |  |  | (requirements of IEC 60529 and IEC 60034-5 for IP5X) |  |  |  |  |  |  |  |
|  | first numeral ( |  |  |  |  | ), IEC 60529, Cl |  |  |  |  | ; |  |  |  |  |  |  |
| applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| details of tests:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Dust-tight apparatus to Practice B: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | heat cycling test; |  |  |  |  |  |  | operated at rated load until maximum temperature reached, then allowed to cool to room temperature for at least six cycles and a minimum time of 30 h |  |  |  |  |  |  |  |  |  |
| applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| details of tests:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | no visible dust entered the enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | joints comply with clause 3.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Dust-protected apparatus to Practice B: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | heat cycling test; |  |  |  |  |  |  | operated at rated load until maximum temperature reached then allowed to cool to room temperature for at least two cycles and a minimum time of 10 h |  |  |  |  |  |  |  |  |  |
| applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| details of tests:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | no visible dust entered the enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 10 of 45 	(IEC 61241-1-1, 1993)

| ###### IEC 61241-1-1 |  |  |  |  | VERIFICATION AND TESTS 2/2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | YES |  |  |  | NO | ENCL. |  |  |  |  |  |
| 4.3 |  |  |  |  | Thermal tests |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thermal tests |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Temperature measurement: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| apparatus input ratings: |  |  |  |  |  |  |  |  |  | V ( |  |  |  |  | Hz / |  |  |  |  | d.c.), |  |  |  |  |  | A, |  |  | W/ |  |  | VA |  |  |
| conditions of loading: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Note: The most unfavourable voltage within 90% and 110% of the nominal input voltage shall be applied. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | apparatus mounted in normal service position ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |  |
|  |  | apparatus tested in different normally used positions; highest temperature (see data below) with (position): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Note: The position resulting in the highest temperature shall be marked on the apparatus |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | continued until rate of rise of temperature  2 K/h |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature data: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Location |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Temperature |  |  |  |  |  |  |  |  |  |
|  | component/surface/part |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Method |  |  |  |  |  | C |  |  |  |
|  | ambient |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Maximum temperature ( |  |  |  |  |  |  |  |  | C), corrected for:- |  |  |  |  |  |  |  |  |  |  | 40 C Ambient to |  |  |  |  |  |  |  |  | C or |  |  |  |  |  |
| * |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C Ambient to |  |  |  |  |  |  | C |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | *(maximum ambient temperature specified for the apparatus) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature control: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | temperature protection not defeated during the thermal tests |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ambient temperature range: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | -20 to +40 C or ( |  |  |  |  |  |  |  |  |  |  |  |  | C ; |  |  |  |  |  | marked accordingly) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Apparatus Practice A: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | thermal test performed without dust layers on the enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | maximum surface temperature if the enclosure TA is the temperature measured during the thermal test, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | corrected to 40 C Ambient; TA |  |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Apparatus Practice B: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | thermal test performed with maximum covering of dust layer on the enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | maximum surface temperature if the enclosure TB is the temperature measured during the thermal test, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | corrected to 40 C Ambient; TB |  |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 11 of 45 	(IEC 61241-1-1, 1993)

| ###### IEC 61241-1-1 |  |  | MARKING 1/1 |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  |  | YES |  | NO |  | ENCL. |  |  |
| 5.1 |  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.2 |  |  | Markings |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Marking visible, legible, durable and on the main part of the equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Markings |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Marking on all apparatus shall include: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Manufacturer's name |  |  |  | Registered trademark |  |  |  |  |  |  |  |  |  |  |  |
| Product identification: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Manufacturer's type identification |  |  |  |  |  |  | Serial number |  |  |  |  |  |  |  |  |
| Other: (e.g. as normally required by the standards of construction of the electrical apparatus) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Supplementary marking of apparatus to practice A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | For use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The symbol DIP |  |  |  |  | DIP |  |  | Name, mark of certifying authority & reference |  |  |  |  |  |  |  |  |
| The letter signs : |  |  |  |  | DIP |  |  | A |  |  |  |  |  | 21 |  |  |
|  | Maximum surface temperature TA or temperature class |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | For use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The letter signs : |  |  |  |  | DIP |  |  | A |  |  |  |  |  | 22 |  |  |
|  | Maximum surface temperature TA or temperature class |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Supplementary marking of apparatus to practice B |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | For use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The symbol DIP |  |  |  |  | DIP |  |  | Name, mark of certifying authority & reference |  |  |  |  |  |  |  |  |
| The letter signs : |  |  |  |  | DIP |  |  | B |  |  |  |  |  | 21 |  |  |
|  | Maximum surface temperature TB or temperature class |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | For use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The letter signs : |  |  |  |  | DIP |  |  | B |  |  |  |  |  | 22 |  |  |
|  | Maximum surface temperature TB or temperature class |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method of marking |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 12 of 45 	(IEC 61241-1-1, 1993)

| IEC 61241-1-1 |  | COMMENTS |  |  |
| --- | --- | --- | --- | --- |
| #### Clause |  |  | Page |  |

Sheet 13 of 45

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION TWO  ALL APPARATUS 1/7 |  |  |  |  |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  | YES | NO |  | ENCL. |  |  |
| 5 |  |  |  | General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  | Enclosures of plastics material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | The electrical apparatus is suitable for industrial use as indicated and confirmed by the manufacturer: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | - by declaring compliance with appropriate national or internationally recognized standards (affidavit attached) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | - (other method) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Delayed opening of enclosures: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Internal capacitance |  |  |  |  |  |  |  |  | T Class |  | Max. Internal Temperature |  |  |  |  |  | Components considered |  |  |  |
|  | Required limiting value of residual energy (mJ) |  |  |  |  |  | Time to discharge to limiting value |  |  |  |  | Component temperature (C) |  |  | Time to cool to value < T Class |  |  |  |  |  |  |
|  | 0.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Time required to open the apparatus, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | A label stating the required delay time is provided ; refer to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Drainage: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | device(s) fitted; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Refer to form for specific type of protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Enclosures of plastics material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Manufacturer's type and generic name of material: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Composition of material: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Minimum thickness (mm) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Refer to SECTION FOUR  VERIFICATIONS AND TESTS, Thermal stability of plastics enclosures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Holes for fasteners of covers removable in service: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | tapped metal inserts; details of method establishing permanency of fixing inserts in plastics material: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | tapped holes for metal fasteners; details of compatible thread size/form/depth of tapping, fastener type/length: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | tapped holes for plastics fasteners; details of compatible thread size/form/depth of tapping, fastener |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | type/length: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 2/7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 14 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  |  | SECTION TWO  ALL APPARATUS 2/7 |  |  |  |  |  |  |  |  |  | # APPLIED |  |  |  |  |
| ###### CLAUSE |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | YES | NO | ENCL. |  |  |
| 6 |  |  |  |  |  | Enclosures of plastics material (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  | Fasteners |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Enclosures of plastics material (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Electrostatic discharge: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Group |  |  | Surface area not subject to test (cm2) |  |  |  |  |  | Actual surface area (cm2) |  |  | Insulation resistanceb () |  | Enclosure surface or part considered |  |  |  |  |  |
|  | I |  |  |  100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IIA, IIB |  |  |  100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  400a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IIC |  |  |  20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  100a |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| aWhere the plastics material is surrounded by conductive earthed frames bA warning label is required where insulation resistance exceeds 1 G |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Refer to SECTION FOUR  VERIFICATIONS AND TESTS, Insulation resistance test of plastic parts |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Refer to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fasteners (used on |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |  |
|  |  | Refer to form(s) for specific type(s) of protection ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |  |
| Fastenings necessary to achieve a standard type of protection or to prevent access to uninsulated live parts: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | removable only by use of a tool; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fastening screws: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | applied to light alloy enclosure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | applied to enclosure of; (material) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | screws of light alloy; (composition) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | screws of other material ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |  |
|  |  | screw head type: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | compatible with enclosure material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Threaded holes for fasteners of covers removable in service: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | thread-form is compatible with enclosure material; details of size, form and depth of tapping: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 15 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  |  | SECTION TWO  ALL APPARATUS 3/7 |  |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  | YES |  | NO |  | ENCL. |  |  |  |
| 9 |  |  |  |  |  | ###### Interlocking devices maintaining a type of protection |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  | Bushings and terminal studs |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  | ###### Cementing and sealing materials |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Interlocking devices maintaining a type of protection ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| Details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | interlocking device cannot be defeated by the use of normally available tools |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bushings and terminal studs ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| Means to prevent turning: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Refer to SECTION FOUR  VERIFICATIONS AND TYPE TESTS, Torque tests for bushings and terminal studs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cementing and sealing materials (Note: Not including gaskets.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Purpose: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Material: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Properties: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistant to water, oil, solvents and similar external influences: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | YES |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | NO; (details of additional protection) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thermal stability evaluation: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Temperatures to which the material will be subjected, based on apparatus rating:- |  |  |  |  |  |  |  |  |  |  |  |  |  | lowest, |  |  | C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | highest, |  |  | C |  |
|  | Verification of material stability; (method): |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |
|  | at lowest temperature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | at greater of 20 K above highest temperature or 120 C ( |  |  |  |  |  |  |  |  |  | C ): |  | Results |  |  |  |  |  |  |

Sheet 16 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  | SECTION TWO  ALL APPARATUS 4/7 |  |  |  |  |  |  |  | APPLIED |  |  |  |  |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  | YES | NO | ENCL. |  |  |
| 12 |  |  |  |  | Connections |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  | Connection facilities for earthing or equipotential bonding conductors |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Connections ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |  |
|  | Connecting means |  |  |  |  |  |  |  | Insulating material |  |  | Characteristics ensuring that contact pressure is not affected by dimensional changes of insulating material in service |  |  |  |  |  |
|  | Identification |  |  |  |  | Type of terminal |  |  | Composition |  |  |  |  |  |  |  |  |
| Connection facilities for earthing or equipotential bonding conductors |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Provision for connection of earthing or equipotential bonding conductor: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | not required; reason:- |  |  |  |  |  | apparatus, portable while energized, having appropriate conductor in supply cable |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | earthing is not necessary; (details) |  |  |  |  |  |  |  |  |  |
|  |  | inside terminal compartment; (location, *capacity and conductor size) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | *Required conductor capacity  4 mm2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | outside metallic enclosure; (location, capacity and conductor size) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | protected against corrosion; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | means to prevent loosening/twisting of conductors; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | means to ensure that contact pressure is maintained; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Light alloy parts are used: |  |  |  |  |  |  |  | NO |  |  | YES; (corrosion protection) |  |  |  |  |  |  |

Sheet 17 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION TWO  ALL APPARATUS 5/7 |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  | YES |  | NO | ENCL. |  |  |
| 14 |  |  |  | Connection facilities and terminal compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  | Cable and conduit entries |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Connection facilities and terminal compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | not required (permanently connected cable) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Terminal compartment for: |  |  |  |  |  |  | Dimensions of terminal compartment |  |  |  |  | Dimensions of access opening |  |  |  |  |
|  |  | design ensures that conductors can be readily connected |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | design ensures that clearances and creepage distances are not compromised by proper connection of conductors |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable and conduit entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Range of cable sizes per manufacturer's specification: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method of mounting: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sealing method: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | asbestos |  |  |  |  | hard setting resin |  |  |  | elastomeric sealing ring |  |  |  |  |  |  |
|  |  | asbestos rope packing |  |  |  |  | hard setting compound |  |  |  | metallic sealing ring (for metal sheathed cable) |  |  |  |  |  |  |
|  |  | details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Features of construction: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | cable passes through enclosure wall without damage; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | for flexible cables, there are no sharp edges for cable movement 90in any direction with respect to entry axis |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | entry point *rounded; (details) |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | *Required radius of curvature  ¼ of the largest size of cable allowed |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | other method; |  |  |  |  |  |  |  |  |  |  |
|  |  | clamping to prevent strain on cable connections; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 6/7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 18 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  | SECTION TWO  ALL APPARATUS 6/7 |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  | YES | NO |  |  | ENCL. |  |  |
| 15 |  |  | Cable and conduit entries (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable and conduit entries (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ###### clamping complies with SECTION FOUR  VERIFICATIONS AND TESTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | ###### Tests of clamping of non-armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | ###### Tests of clamping of armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | compliance verified by test |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | other verification; |  |  |  |  |  |  |  |  |  |  |  |
|  | bonding of armour, sheath or screen; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Entries for conduit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Entry method: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | threaded hole; (size) |  |  |  |  |  |  |  |  |  | 5 full straight threads |  |  |  | 3 full tapered threads |  |  |  |
|  | plain hole; (locking means) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | in enclosure wall(s) or |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | in adaptor plate in/on enclosure; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |
|  | into a stopping box:- |  |  |  |  | integral with wall of enclosure |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | attached to wall of enclosure; (details) |  |  |  |  |  |  |  |  |  |  |  |  |
| Blanking of unused entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | blanking element provided; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Satisfy degree of protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | means ensuring that blanking element is removable only with the aid of a tool; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 7/7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 19 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  | SECTION TWO  ALL APPARATUS 7/7 |  |  |  | APPLIED |  |  |  |  |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  | YES | NO | ENCL. |  |  |
| 15 |  |  | Cable and conduit entries (continued) |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |
| Cable and conduit entries (continued) |  |  |  |  |  |  |  |  |  |  |  |
| Elevated temperature at entries |  |  |  |  |  |  |  |  |  |  |  |
| Temperature under rated conditions (based on |  |  |  |  |  |  |  |  |  | ): |  |
|  | > 70 C at entry point |  |  |  | > 80 C at branching point of conductors |  |  |  |  |  |  |
| User information: |  |  |  |  |  |  |  |  |  |  |  |
|  | label affixed as a guide to selection of cable or wire which may contact parts at elevated temperature; (details): |  |  |  |  |  |  |  |  |  |  |
| Compatibility with type of protection |  |  |  |  |  |  |  |  |  |  |  |
|  | entries do not alter the specific characteristics of the type of protection of the apparatus |  |  |  |  |  |  |  |  |  |  |

Sheet 20 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  |  | SECTION THREE  CERTAIN APPARATUS 1/4 |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  | YES | NO | ENCL. |  |  |  |  |  |
| 16 |  |  |  |  |  | Rotating electrical machines |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rotating electrical machines |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ventilation openings for external fans: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | IP10 on air outlet side ( |  |  |  |  |  |  | objects > 12 mm cannot be carried onto moving parts (Group I); design details: |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |  |
|  |  | IP20 on air inlet side |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ingress protection verified according to IEC 60034-5; (method) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | for vertical machines, means to prevent foreign bodies from falling vertically into ventilation openings: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Construction and mounting of ventilating systems (e.g. fans, fanhoods, screens): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | means preventing distortion and displacement of parts to avoid impact or friction with rotating parts; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | refer to SECTION FOUR  VERIFICATIONS AND TESTS, Test for resistance to impact |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | refer to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Clearances (external fan and hood, screen and fasteners): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Fan max. diameter (mm) |  |  |  |  |  | Clearance (mm) |  |  | Between fan and (part): |  |  |  |  |  |  |  |  |  |  |
| Clearances are required to be  1100 maximum fan diameter and  1mm (clearances need not exceed 5mm) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | allowable minimum clearance of 1mm for machined parts ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |  |
|  |  | clearances measured at rest and under the most unfavourable conditions of movement, prior to mechanical testing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fan material: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | plastics; (composition) |  |  |  |  |  |  |  |  |  | electrical resistance, |  |  |  |  |  |  |  |  |
|  |  | refer to SECTION FOUR  VERIFICATIONS AND TESTS, Insulation resistance test of plastic parts |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Required: resistance  1 G ( |  |  |  |  |  |  |  |  | exception; Group II machine having peripheral fan speed < 50 m/s ( |  |  |  |  |  |  |  | m/s)) |  |  |  |
|  |  | light alloy; (composition) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Contain  6 % magnesium |  |  |  |  |  |  |  | Note: Some countries do not permit the use of some light alloys in mines susceptible to fire-damp. |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | (other) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 21 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION THREE  CERTAIN APPARATUS 2/4 |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | YES |  |  |  | NO |  | ENCL. |  |  |  |
| 17 |  |  |  | Switchgear |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Switchgear |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ratings: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | V |  | a.c. |  | A / |  |  |  |  |  |  | V |  |  | d.c. |  |  |  | A |
| Oil immersed: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | NO |  |  |  |  | YES; apparatus is for a.c. rating only (oil immersion is not permitted for direct current) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | apparatus is for Group I:- |  |  |  |  | for use above 1100 V with |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | each pole segregated and |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | oil content  5 litres per pole |  |  |  |  |  |  |  |  |  |  |  |
| Disconnectors: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | disconnects all poles |  |  |  |  | contact position visible, (or |  |  |  |  | reliably indicated; e.g. "ON/OFF"); details: |  |  |  |  |  |  |  |  |  |  |  |
|  |  | cover/door interlock ( |  |  |  |  | design allows opening only when supply is disconnected ); details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Access covers of remotely operated apparatus: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | interlocked with a disconnector (details; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) or |  |
|  |  | parts remaining energized on opening covers have type of protection " |  |  |  |  |  |  |  |  |  |  |  |  | " (or |  |  |  | IP20 for type "e") or |  |  |  |  |
|  |  | label affixed saying "DO NOT OPEN WHEN ENERGIZED"; (method) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 22 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION THREE  CERTAIN APPARATUS 3/4 |  |  |  |  |  | APPLIED |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  | YES | NO | ENCL. |  |
| 18 |  |  |  | Fuses |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  | Plugs and sockets |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fuses ( |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| Enclosure containing fuse(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | interlocked so that:- |  |  |  |  |  | fuse links can be inserted/removed only with the voltage off and |  |  |  |  |  |  |
|  |  |  |  |  |  |  | the fuse cannot be energized until the enclosure is correctly closed |  |  |  |  |  |  |
|  | details of interlock feature: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | alternatively, a label is affixed saying "DO NOT OPEN WHEN ENERGIZED"; method: |  |  |  |  |  |  |  |  |  |  |  |  |
| Plugs and sockets ( |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| Interlocked: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | mechanically or |  |  |  |  |  | electrically; so that:- |  | they cannot be separated with contacts energized |  |  |  |  |
| and |  |  |  |  |  |  |  |  | they cannot be energized when separated |  |  |  |  |
|  | details; |  |  |  |  |  |  |  |  |  |  |  |  |
| Not interlocked: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | fixed together by special fasteners (refer to SECTION TWO  ALL APPARATUS 3/7, Fasteners) and |  |  |  |  |  |  |  |  |  |  |  |  |
|  | bearing a label "DO NOT OPEN WHEN ENERGIZED"; (method) |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 23 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  | SECTION THREE  CERTAIN APPARATUS 4/4 |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  | YES | NO |  |  | ENCL. |  |  |  |
| 20 |  |  |  |  | Luminaires |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 21 |  |  |  |  | Hand lamps and cap lamps |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Luminaires |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Type of lamp and ratings: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Note: Lamps containing free metallic sodium (e.g. low pressure sodium lamps) are not permissible. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Light transmitting cover of |  |  |  |  |  |  |  |  |  |  |  | , |  |  | mm thick |  |  |
|  |  | Optional protective guard; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Supply interlocking feature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | YES; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | NO (alternatively, |  |  |  |  | a label is affixed reading "DO NOT OPEN WHEN ENERGIZED"); method: |  |  |  |  |  |  |  |  |  |  |  |  |
| Hand lamps and cap lamps |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Battery: type |  |  |  |  |  |  |  |  | ; electrolyte |  |  |  |  |  |  |  |  |  |  |
| Materials of construction: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Part |  |  |  |  | Composition |  |  |  | Verification of resistance to electrolyte |  |  |  |  |  |  |  |  |  |
| Measures to prevent leakage of electrolyte, considering all positions of the apparatus: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Connecting cable for separately enclosed light source and supply source: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | cable and cable entries withstand a tensile load (pull) of 150 N; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | refer to VERIFICATIONS AND TESTS, Clamping |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | refer to |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | cable sheath material is oil resistant and flame retardant; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 24 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  |  |  | SECTION FOUR  VERIFICATIONS AND TESTS 1/6 |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |
| ###### CLAUSE |  |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  | YES | NO | ENCL. |  |  |
| 22.2 |  |  |  |  |  |  | Verification of documents |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.3 |  |  |  |  |  |  | Compliance of prototype or sample with documents |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.4.1, 22.4.2 |  |  |  |  |  |  | Type tests, General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.4.3.1 |  |  |  |  |  |  | Test for resistance to impact |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verification of documents |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The manufacturer's documents that were considered in the evaluation are listed in this report. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The manufacturer's documents specifying the design and the safety aspects of the electrical apparatus address the requirements of IEC 60079-0 and those parts of IEC Publication 60079 specific to the type of protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Compliance of prototype or sample with documents |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A prototype or sample of the electrical apparatus was found to comply with the listed definitive documents. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Type tests, General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The prototype/sample was tested in accordance with the requirements of IEC 60079-0 and those parts of IEC Publication 60079 specific to the type of protection concerned. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Note: Tests shall be made in the laboratory of the national or other appropriate authority or elsewhere under the supervision of that authority. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Accessories per the manufacturer's descriptive literature for the apparatus were included for each test; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Note: The manufacturers of standardized accessories need not be identified if their design is completely defined. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test for resistance to impact |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Refer to form(s) for specific type(s) of protection ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| Light transmitting part with guard (tested without guard); |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | : |
|  | normal risk of mechanical damage; impact energy E:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 joules (Group II) |  |  |  |  |  |  |
|  | low risk of mechanical damage; impact energy E:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1 joule (Group II) |  |  |  |  |  |  |
| Light transmitting part without guard; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | : |
|  | normal risk of mechanical damage; impact energy E:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4 joules (Group II) |  |  |  |  |  |  |
|  | low risk of mechanical damage; impact energy E:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 joules (Group II) |  |  |  |  |  |  |
| For a light transmitting part, |  |  |  |  |  |  |  |  |  | one sample was tested |  |  |  |  |  | three samples were tested, once each (glass parts) |  |  |  |  |  |  |
| Enclosure or part of enclosure; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | : |
|  | normal risk of mechanical damage; impact energy E:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 7 joules (Group II) |  |  |  |  |  |  |
|  | low risk of mechanical damage; impact energy E:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4 joules (Group II) |  |  |  |  |  |  |
|  | Note: Where low risk of mechanical damage is assessed, the apparatus shall be marked "X" |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Impact applied in direction |  |  |  |  |  |  |  |  |  | normal to flat surface |  |  |  |  |  | normal to tangent at point of impact |  |  |  |  |  |  |
| Note: An example of the standard free fall test fixture for fixed apparatus is shown in Appendix A. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Temperature of sample: |  |  |  |  |  |  |  |  |  | 25  10 C (metal) |  |  |  |  |  |  |  |  |  |  |  |  |
| (plastics) |  |  |  |  |  |  |  | C |  | service temperature ( |  |  |  |  |  |  | C) + 10 K with a minimum of 50 C and |  |  |  |  |  |
| (plastics) |  |  |  |  |  |  |  | C |  | 25  3 C (except 5  3 C if for use inside buildings) on a second sample |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | Note: Electrical apparatus restricted to use inside buildings shall be marked accordingly. |  |  |  |  |  |  |  |  |  |  |  |  |
| Results: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 25 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  |  |  |  | SECTION FOUR  VERIFICATIONS AND TESTS 2/6 |  |  |  |  |  | APPLIED |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  | YES | NO |  | ENCL. |  |  |  |
| 22.4.3.2 |  |  |  |  |  |  |  | Drop tests |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.4.5 |  |  |  |  |  |  |  | Torque tests for bushings and terminal studs |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.4.6.2 |  |  |  |  |  |  |  | Thermal stability of plastics enclosures |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Drop tests (portable apparatus) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | refer to form(s) for specific type(s) of protection ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
|  | Sample positioning for drop: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Temperature of sample:- |  |  |  |  |  |  |  |  |  | 25  10 C (non-plastics enclosed apparatus) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 25  3 C (apparatus having enclosure or parts of enclosure of plastics material) |  |  |  |  |  |  |  |  |  |
|  |  | sample, ready for use, dropped four times from a height of 1 m on a horizontal concrete surface |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Results: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Torque tests for bushings and terminal studs (used for connection purposes) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Torque (for stem size): |  |  |  |  |  |  |  |  |  |  | 2.0 Nm (M4) |  | 3.2 Nm (M5) |  |  | 5 Nm (M6) |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 10 Nm (M8) |  | 16 Nm (M10) |  |  | 25 Nm (M12) |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 50 Nm (M16) |  | 85 Nm (M20) |  |  | 130 Nm (M24) |  |  |  |  |
| Method of applying torque: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | to terminal stud; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | to bushing; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Results: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thermal stability of plastics enclosures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | four weeks storage at:- |  |  |  |  |  |  |  |  |  90% relative humidity and |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 20 K above maximum service temperature (80 C minimum), |  |  |  |  |  |  |  | C |  |
|  |  | 24 h storage at 30  3 C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | conditioning did not invalidate the type(s) of protection of the apparatus, as determined by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 26 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  | SECTION FOUR  VERIFICATIONS AND TESTS 3/6 |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | YES |  | NO |  |  | ENCL. |  |  |  |  |
| 22.4.6.3 |  |  |  |  | Thermal shock test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.4.7 |  |  |  |  | Insulation resistance test of plastic parts |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thermal shock test (glass parts of luminaires and windows of apparatus) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | subjected to a jet of water  1mm dia. at 10  5 C with glass part at max. service temperature ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | C) |  |
| Breakage of glass part(s): |  |  |  |  |  |  |  | NO |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | YES (details): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Insulation resistance test of plastic parts |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Preparation of test specimen: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | using intact surface of |  |  |  |  |  |  | part itself or |  | test piece at least 149 mm by 59.5 mm; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | two parallel electrodes painted per FIG. 2, using conducting paint ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| Note: Conducting paint solvent must not affect the insulation resistance. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Part cleaned with (in turn): |  |  |  |  |  |  |  | distilled water |  | *isopropyl alcohol |  |  |  |  |  |  |  | distilled water |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | *alternatively, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| *Note: Alternative solvent must be miscible with water and must not affect specimen material. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Part conditioned for 24 h in a clean atmosphere at:- |  |  |  |  |  |  |  |  | 23  2 C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | relative humidity between 48% and 52% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: Following cleaning the part must be subjected to conditioning without being touched by hand. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 500 V  10 V d.c. applied between electrodes for 1 min. |  |  |  |  |  |  |  |  |  | Note: Applied voltage shall be sufficiently steady for the charging current due to voltage fluctuation to be negligible compared with current flowing through the test piece. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Insulation resistance = |  |  |  |  |  | d.c. voltage applied between electrodes |  |  |  |  |  | = |  |  |  |  |  | = |  |  |  |  |  |  |
|  |  |  |  |  |  | total current flowing between electrodes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Note: The voltage and current are determined when the voltage has been applied for 1 min. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method of measurement: (see Appendix B for possible methods) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 27 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION FOUR  VERIFICATIONS AND TESTS 4/6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | YES |  |  |  | NO |  |  | ENCL. |  |  |  |
| 22.4.9 |  |  |  | Tests of clamping of non-armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tests of clamping of non-armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Allowable cable sizes/size ranges: |  |  |  |  |  |  |  |  |  |  | 1) |  |  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |  |  |  |  |
| Clamping |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| For elastomeric sealing rings: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The sealing ring was mounted on a clean, dry polished, cylindrical mild steel mandrel of a diameter equal to the smallest cable diameter allowable in the ring as specified by the manufacturer of the cable entry. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Mandrel sizes used: |  |  |  |  | 1) |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  |
|  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |
| For metallic sealing rings: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The sealing ring was mounted on the metallic sheath of a sample of clean dry cable of diameter equal to the smallest allowable in the ring as specified by the manufacturer of the cable entry. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable type(s) used: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable sizes used: |  |  |  |  | 1) |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  |
|  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |
| Other sealing methods: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The cable entry was prepared according to the manufacturer's instructions using the prescribed sealing material and sizes of cable samples. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable type(s) used: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable sizes used: |  |  |  | 1) |  |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  |
|  |  |  |  |  | 4) |  |  |  |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |
| Preparation of test samples (cable entry assembly mounted on a tensile test machine): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The sealing ring was compressed while observing in each case the value of tightening torque necessary to prevent slipping of the mandrel or cable with applied force equal to 20 times the value in mm of the mandrel or cable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Tensile force: |  |  |  |  | 1) |  |  |  |  |  |  | N |  | 2) |  |  |  |  |  | N |  | 3) |  |  |  |  |  | N |  |
|  |  |  |  |  |  | 4) |  |  |  |  |  |  | N |  | 5) |  |  |  |  |  | N |  | 6) |  |  |  |  |  | N |  |
|  | Tightening torque: |  |  |  |  | 1) |  |  |  |  |  |  | Nm |  | 2) |  |  |  |  |  | Nm |  | 3) |  |  |  |  |  | Nm |  |
|  |  |  |  |  |  | 4) |  |  |  |  |  |  | Nm |  | 5) |  |  |  |  |  | Nm |  | 6) |  |  |  |  |  | Nm |  |
| Test procedure: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 110% of the tightening torque determined above was applied to the cable entry clamping screws or nut. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A constant tensile force equal to that defined above was maintained for 6 h. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Slipping of mandrel or cable sample:  6mm is acceptable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | 1) |  |  |  |  |  |  | mm |  | 2) |  |  |  |  |  | mm |  | 3) |  |  |  | mm |  |  |
|  |  |  |  |  |  |  | 4) |  |  |  |  |  |  | mm |  | 5) |  |  |  |  |  | mm |  | 6) |  |  |  | mm |  |  |
| continued on 5/6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 28 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION FOUR  VERIFICATIONS AND TESTS 5/6 |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  | YES |  |  |  |  | NO |  | ENCL. |  |  |  |  |
| 22.4.9 |  |  |  | Tests of clamping of non-armoured cables in cable entries (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.4.10 |  |  |  | ###### Tests of clamping of armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tests of clamping of non-armoured cables in cable entries (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mechanical strength (Note: The cable entry is removed from the tensile test machine for this test.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Twice the tightening torque that prevents slipping was applied to the cable entry clamping screws or nut. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Results of examination of components (sample dismantled): Required: No noticeable damage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1) |  |  |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3) |  |  |  |  |  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5) |  |  |  |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Note: Sealing ring deformation shall be ignored. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tests of clamping of armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Allowable cable sizes/size ranges: |  |  |  |  |  |  | 1) |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |  |  |  |  |  |
| Clamping |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A sample of armoured cable of the smallest diameter allowable as specified by the manufacturer of the cable entry was fitted into the clamping device. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable samples; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable sizes used: |  |  |  | 1) |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  |
|  |  |  |  |  | 4) |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |
| Preparation of test samples (cable entry assembly mounted on a tensile test machine): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The clamping device was tightened while observing in each case the value of minimum torque necessary to prevent slipping of the cable with applied force equal to 80 times the value in mm of the cable over the armour. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Tensile force: |  |  |  | 1) |  |  |  |  | N |  |  | 2) |  |  |  |  |  |  | N |  | 3) |  |  |  | N |  |  |
|  |  |  |  |  | 4) |  |  |  |  | N |  |  | 5) |  |  |  |  |  |  | N |  | 6) |  |  |  | N |  |  |
|  | Tightening torque: |  |  |  | 1) |  |  |  |  | Nm |  |  | 2) |  |  |  |  |  | Nm |  |  | 3) |  |  |  |  | Nm |  |
|  |  |  |  |  | 4) |  |  |  |  | Nm |  |  | 5) |  |  |  |  |  | Nm |  |  | 6) |  |  |  |  | Nm |  |
| Test procedure: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A constant tensile force equal to that defined above was maintained for 2 min. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Slipping of the cable armour: Required to be effectively zero |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1) |  |  |  | mm |  |  | 2) |  |  |  |  |  | mm |  |  | 3) |  |  |  | mm |  |  |  |
|  |  |  |  |  | 4) |  |  |  | mm |  |  | 5) |  |  |  |  |  | mm |  |  | 6) |  |  |  | mm |  |  |  |
| Mechanical strength (Note: The cable entry is removed from the tensile test machine for this test) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 2  the tightening torque determined in the clamping test was applied to the cable entry clamping screws or nut. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Results of examination of components (sample dismantled): Required: No noticeable damage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1) |  |  |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3) |  |  |  |  |  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5) |  |  |  |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 29 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT A Apparatus for use in zone 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  | SECTION FOUR  VERIFICATIONS AND TESTS 6/6 |  |  |  |  |  | APPLIED |  |  |  |  |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  | YES |  | NO | ENCL. |  |
| 23 |  |  |  |  | Routine verifications and tests |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Routine verifications and tests |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: 1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to forms for specific types of protection: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to specification(s) submitted per definitive documents list , Item(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | per established procedure(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: 2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to forms for specific types of protection: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to specification(s) submitted per definitive documents list, Item(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | per established procedure(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: 3) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to forms for specific types of protection: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to specification(s) submitted per definitive documents list, Item(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | per established procedure(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: 4) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to form(s) for specific type(s) of protection: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to specification(s) submitted per definitive documents list, Item(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | per established procedure(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 30 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  | SECTION TWO  ALL APPARATUS 1/7 |  |  |  |  | # APPLIED |  |  |  |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  |  | YES | NO | ENCL. |  |
| 5 |  |  | General |  |  |  |  |  |  |  |  |
| 6 |  |  | Enclosures of plastics material |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |
| General |  |  |  |  |  |  |  |  |  |  |  |
|  | The electrical apparatus is suitable for industrial use as indicated and confirmed by the manufacturer: |  |  |  |  |  |  |  |  |  |  |
|  | - by declaring compliance with appropriate national or internationally recognized standards (affidavit attached) |  |  |  |  |  |  |  |  |  |  |
|  | - (other method) |  |  |  |  |  |  |  |  |  |  |
| Drainage: |  |  |  |  |  |  |  |  |  |  |  |
|  | device(s) fitted; (details) |  |  |  |  |  |  |  |  |  |  |
|  | Refer to form for specific type of protection |  |  |  |  |  |  |  |  |  |  |
| Enclosures of plastics material |  |  |  |  |  |  |  |  |  |  |  |
| Manufacturer's type and generic name of material: |  |  |  |  |  |  |  |  |  |  |  |
| Composition of material: |  |  |  |  |  |  |  |  |  |  |  |
| Minimum thickness (mm) |  |  |  |  |  |  |  |  |  |  |  |
| Holes for fasteners of covers removable in service: |  |  |  |  |  |  |  |  |  |  |  |
|  | tapped metal inserts; details of method establishing permanency of fixing inserts in plastics material: |  |  |  |  |  |  |  |  |  |  |
|  | tapped holes for metal fasteners; details of compatible thread size/form/depth of tapping, fastener type/length: |  |  |  |  |  |  |  |  |  |  |
|  | tapped holes for plastics fasteners; details of compatible thread size/form/depth of tapping, fastener |  |  |  |  |  |  |  |  |  |  |
|  | type/length: |  |  |  |  |  |  |  |  |  |  |

Sheet 31 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION TWO  ALL APPARATUS 2/7 |  |  |  |  |  | # APPLIED |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  | YES | NO | ENCL. |  |
| 8 |  |  |  | Fasteners |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fasteners |  |  | (used on |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
|  | Refer to form(s) for specific type(s) of protection ( |  |  |  |  |  |  |  |  |  |  |  | ) |
| Fastenings necessary to achieve a standard type of protection or to prevent access to uninsulated live parts: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | removable only by use of a tool; (details) |  |  |  |  |  |  |  |  |  |  |  |  |
| Fastening screws: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | applied to light alloy enclosure |  |  |  |  |  |  |  |  |  |  |  |  |
|  | applied to enclosure of; (material) |  |  |  |  |  |  |  |  |  |  |  |  |
|  | screws of light alloy; (composition) |  |  |  |  |  |  |  |  |  |  |  |  |
|  | screws of other material ( |  |  |  |  |  |  |  |  |  |  |  | ) |
|  | screw head type: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | compatible with enclosure material |  |  |  |  |  |  |  |  |  |  |  |  |
| Threaded holes for fasteners of covers removable in service: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | thread-form is compatible with enclosure material; details of size, form and depth of tapping: |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 32 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  |  |  | SECTION TWO  ALL APPARATUS 3/7 |  |  |  |  | # APPLIED |  |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  |  |  |  | REQUIREMENTS |  |  |  |  | YES |  | NO |  | ENCL. |  |  |  |
| 9 |  |  |  |  |  |  | ###### Interlocking devices maintaining a type of protection |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  | Bushings and terminal studs |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  | ###### Cementing and sealing materials |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Interlocking devices maintaining a type of protection ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| Details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | interlocking device cannot be defeated by the use of normally available tools |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bushings and terminal studs ( |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| Means to prevent turning: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cementing and sealing materials (Note: Not including gaskets.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Purpose: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Material: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Properties: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Resistant to water, oil, solvents and similar external influences: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | YES |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | NO; (details of additional protection) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thermal stability evaluation: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Temperatures to which the material will be subjected, based on apparatus rating:- |  |  |  |  |  |  |  |  |  |  |  |  | lowest, |  |  | C |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | highest, |  |  | C |  |
|  | Verification of material stability; (method): |  |  |  |  |  |  |  |  |  |  |  | Results |  |  |  |  |  |  |
|  |  | at lowest temperature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | at greater of 20 K above highest temperature or 120 C ( |  |  |  |  |  |  |  |  | C ): |  | Results |  |  |  |  |  |  |

Sheet 33 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  | SECTION TWO  ALL APPARATUS 4/7 |  |  |  |  |  | APPLIED |  |  |  |  |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  | YES | NO | ENCL. |  |  |
| 12 |  |  |  |  | Connections |  |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  | Connection facilities for earthing or equipotential bonding conductors |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Connections ( |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |  |
|  | Connecting means |  |  |  |  |  |  |  | Insulating material | Characteristics ensuring that contact pressure is not affected by dimensional changes of insulating material in service |  |  |  |  |  |
|  | Identification |  |  |  |  | Type of terminal |  |  | Composition |  |  |  |  |  |  |
| Connection facilities for earthing or equipotential bonding conductors |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Provision for connection of earthing or equipotential bonding conductor: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | not required; reason:- |  |  |  |  |  | apparatus, portable while energized, with appropriate conductor in supply cable |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | earthing is not necessary; (details) |  |  |  |  |  |  |  |
|  |  | inside terminal compartment; (location, *capacity and conductor size) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | *Required conductor capacity  4 mm2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | outside metallic enclosure; (location, capacity and conductor size) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | protected against corrosion; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | means to prevent loosening/twisting of conductors; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | means to ensure that contact pressure is maintained; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Light alloy parts are used: |  |  |  |  |  |  |  | NO |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | YES; (corrosion protection) |  |  |  |  |  |  |  |

Sheet 34 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION TWO  ALL APPARATUS 5/7 |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  | YES |  | NO | ENCL. |  |  |
| 14 |  |  |  | Connection facilities and terminal compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  | Cable and conduit entries |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Connection facilities and terminal compartments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | not required (permanently connected cable) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Terminal compartment for: |  |  |  |  |  |  | Dimensions of terminal compartment |  |  |  |  | Dimensions of access opening |  |  |  |  |
|  |  | design ensures that conductors can be readily connected |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | design ensures that clearances and creepage distances are not compromised by proper connection of conductors |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable and conduit entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Range of cable sizes per manufacturer's specification: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method of mounting: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sealing method: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | asbestos |  |  |  |  | hard setting resin |  |  |  | elastomeric sealing ring |  |  |  |  |  |  |
|  |  | asbestos rope packing |  |  |  |  | hard setting compound |  |  |  | metallic sealing ring (for metal sheathed cable) |  |  |  |  |  |  |
|  |  | details; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Features of construction: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | cable passes through enclosure wall without damage; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | for flexible cables, there are no sharp edges for cable movement 90in any direction with respect to entry axis |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | entry point *rounded; (details) |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | *Required radius of curvature  ¼ of the largest size of cable allowed |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | other method; |  |  |  |  |  |  |  |  |  |  |
|  |  | clamping to prevent strain on cable connections; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 6/7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 35 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  | SECTION TWO  ALL APPARATUS 6/7 |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  | YES | NO |  |  | ENCL. |  |  |
| 15 |  |  | Cable and conduit entries (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cable and conduit entries (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ###### clamping complies with SECTION FOUR  VERIFICATIONS AND TESTS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | ###### Tests of clamping of non-armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | ###### Tests of clamping of armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | compliance verified by test |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | other verification; |  |  |  |  |  |  |  |  |  |  |  |
|  | bonding of armour, sheath or screen; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Entries for conduit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Entry method: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | threaded hole; (size) |  |  |  |  |  |  |  |  |  | 5 full straight threads |  |  |  | 3 full tapered threads |  |  |  |
|  | plain hole; (locking means) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | in enclosure wall(s) or |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | in adaptor plate in/on enclosure; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |
|  | into a stopping box:- |  |  |  |  | integral with wall of enclosure |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | attached to wall of enclosure; (details) |  |  |  |  |  |  |  |  |  |  |  |  |
| Blanking of unused entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | blanking element provided; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | satisfy degree of protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | means ensuring that blanking element is removable only with the aid of a tool; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| continued on 7/7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 36 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  | SECTION TWO  ALL APPARATUS 7/7 |  |  |  | APPLIED |  |  |  |  |
| ###### CLAUSE |  |  | REQUIREMENTS |  |  |  | YES | NO | ENCL. |  |  |
| 15 |  |  | Cable and conduit entries (continued) |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |
| Cable and conduit entries (continued) |  |  |  |  |  |  |  |  |  |  |  |
| Elevated temperature at entries |  |  |  |  |  |  |  |  |  |  |  |
| Temperature under rated conditions (based on |  |  |  |  |  |  |  |  |  | ): |  |
|  | > 70 C at entry point |  |  |  | > 80 C at branching point of conductors |  |  |  |  |  |  |
| User information: |  |  |  |  |  |  |  |  |  |  |  |
|  | label affixed as a guide to selection of cable or wire which may contact parts at elevated temperature; (details): |  |  |  |  |  |  |  |  |  |  |
| Compatibility with type of protection |  |  |  |  |  |  |  |  |  |  |  |
|  | entries do not alter the specific characteristics of the type of protection of the apparatus |  |  |  |  |  |  |  |  |  |  |

Sheet 37 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  | SECTION THREE  CERTAIN APPARATUS 1/3 |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  | YES |  | NO |  | ENCL. |  |  |
| 16 |  |  |  |  | Rotating electrical machines |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 |  |  |  |  | Switchgear |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rotating electrical machines |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ventilation openings for external fans: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | IP10 on air outlet side ( |  |  |  |  |  | objects > 12 mm cannot be carried onto moving parts (Group I); design details: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ) |
|  |  | IP20 on air inlet side |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ingress protection verified according to IEC 60034-5; (method) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Construction and mounting of ventilating systems (e.g. fans, fanhoods, screens): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | means preventing distortion and displacement of parts to avoid impact or friction with rotating parts; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | refer to SECTION FOUR  VERIFICATIONS AND TESTS, Test for resistance to impact |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | refer to |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Switchgear |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ratings: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | V |  | a.c. |  |  | A / |  |  |  |  | V |  | d.c. |  |  | A |
| Oil immersed: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | NO |  |  |  |  |  | YES; apparatus is for a.c. rating only (oil immersion is not permitted for direct current) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | apparatus is for Group I:- |  |  |  |  |  | for use above 1100 V with |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | each pole segregated and |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | oil content  5 litres per pole |  |  |  |  |  |  |  |
| Disconnectors: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | disconnects all poles |  |  |  |  |  | contact position visible, (or |  |  |  |  |  | reliably indicated; e.g. "ON/OFF"); details: |  |  |  |  |  |  |  |
|  |  | cover/door interlock ( |  |  |  |  |  | design allows opening only when supply is disconnected ); details: |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 38 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION THREE  CERTAIN APPARATUS 2/3 |  |  |  |  |  | APPLIED |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  | YES | NO | ENCL. |  |
| 18 |  |  |  | Fuses |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  | Plugs and sockets |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fuses ( |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| Enclosure containing fuse(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | interlocked so that:- |  |  |  |  |  | fuse links can be inserted/removed only with the voltage off and |  |  |  |  |  |  |
|  |  |  |  |  |  |  | the fuse cannot be energized until the enclosure is correctly closed |  |  |  |  |  |  |
|  | details of interlock feature: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | alternatively, a label is affixed saying "DO NOT OPEN WHEN ENERGIZED"; method: |  |  |  |  |  |  |  |  |  |  |  |  |
| Plugs and sockets ( |  |  |  |  |  |  |  |  |  |  |  |  | ) |
| Interlocked: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | mechanically or |  |  |  |  |  | electrically; so that:- |  | they cannot be separated with contacts energized |  |  |  |  |
| and |  |  |  |  |  |  |  |  | they cannot be energized when separated |  |  |  |  |
|  | details; |  |  |  |  |  |  |  |  |  |  |  |  |
| Not interlocked: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | fixed together by special fasteners (refer to SECTION TWO  ALL APPARATUS 3/7, Fasteners) and |  |  |  |  |  |  |  |  |  |  |  |  |
|  | bearing a label "DO NOT OPEN WHEN ENERGIZED"; (method) |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 39 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  | SECTION THREE  CERTAIN APPARATUS 3/3 |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  |  | YES | NO |  |  | ENCL. |  |  |  |
| 20 |  |  |  |  | Luminaires |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 21 |  |  |  |  | Hand lamps and cap lamps |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Luminaires |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Type of lamp and ratings: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Note: Lamps containing free metallic sodium (e.g. low pressure sodium lamps) are not permissible. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Light transmitting cover of |  |  |  |  |  |  |  |  |  |  |  | , |  |  | mm thick |  |  |
|  |  | Optional protective guard; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Supply interlocking feature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | YES; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | NO (alternatively, |  |  |  |  | a label is affixed reading "DO NOT OPEN WHEN ENERGIZED"); method: |  |  |  |  |  |  |  |  |  |  |  |  |
| Hand lamps and cap lamps |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Battery: type |  |  |  |  |  |  |  |  | ; electrolyte |  |  |  |  |  |  |  |  |  |  |
| Materials of construction: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Part |  |  |  |  | Composition |  |  |  | Verification of resistance to electrolyte |  |  |  |  |  |  |  |  |  |
| Measures to prevent leakage of electrolyte, considering all positions of the apparatus: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Connecting cable for separately enclosed light source and supply source: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | cable and cable entries withstand a tensile load (pull) of 150 N; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | refer to VERIFICATIONS AND TESTS, Clamping |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | refer to |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | cable sheath material is oil resistant and flame retardant; (details) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 40 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  |  |  | SECTION FOUR  VERIFICATIONS AND TESTS 1/5 |  |  |  |  |  | APPLIED |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  |  |  |  | REQUIREMENTS |  |  |  |  |  | YES | NO |  | ENCL. |  |  |  |
| 22.2 |  |  |  |  |  |  | Verification of documents |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.3 |  |  |  |  |  |  | Compliance of prototype or sample with documents |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.4.1, 22.4.2 |  |  |  |  |  |  | Type tests, General |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.4.5 |  |  |  |  |  |  | Torque tests for bushings and terminal studs |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.4.6.2 |  |  |  |  |  |  | Thermal stability of plastics enclosures |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Verification of documents |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The manufacturer's definitive documents that were considered in the evaluation are listed in this report. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The manufacturer's definitive documents specifying the design and the safety aspects of the electrical apparatus address the requirements of IEC 60079-0 and those parts of IEC Publication 79 specific to the type of protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Compliance of prototype or sample with documents |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A prototype or sample of the electrical apparatus was found to comply with the listed definitive documents. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Type tests, General |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The prototype/sample was tested in accordance with the requirements of IEC 60079-0 and those parts of IEC Publication 79 specific to the type of protection concerned. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Note: Tests shall be made in the laboratory of the national or other appropriate authority or elsewhere under the supervision of that authority. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Accessories per the manufacturer's descriptive literature for the apparatus were included for each test; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Note: The manufacturers of standardized accessories need not be identified if their design is completely defined. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Torque tests for bushings and terminal studs (used for connection purposes) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Torque (for stem size): |  |  |  |  |  |  |  |  |  | 2.0 Nm (M4) |  | 3.2 Nm (M5) |  |  | 5 Nm (M6) |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 10 Nm (M8) |  | 16 Nm (M10) |  |  | 25 Nm (M12) |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 50 Nm (M16) |  | 85 Nm (M20) |  |  | 130 Nm (M24) |  |  |  |  |
| Method of applying torque: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | to terminal stud; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | to bushing; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Results: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thermal stability of plastics enclosures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | four weeks storage at:- |  |  |  |  |  |  |  |  |  90% relative humidity and |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | 20 K above maximum service temperature (80 C minimum), |  |  |  |  |  |  |  | C |  |
|  | 24 h storage at 30  3 C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | conditioning did not invalidate the type(s) of protection of the apparatus, as determined by: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 41 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION FOUR  VERIFICATIONS AND TESTS 2/5 |  |  | APPLIED |  |  |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  | YES | NO | ENCL. |  |  |  |
| 22.4.6.3 |  |  |  | Thermal shock test |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |
| Thermal shock test (glass parts of luminaires and windows of apparatus) |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |
|  | subjected to a jet of water  1mm dia. at 10  5 C with glass part at max. service temperature ( |  |  |  |  |  |  |  |  |  | C) |  |
| Breakage of glass part(s): |  |  |  |  |  | NO |  |  |  |  |  |  |
|  |  |  |  |  |  | YES (details): |  |  |  |  |  |  |

Sheet 42 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION FOUR  VERIFICATIONS AND TESTS 3/5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | YES |  |  |  | NO |  |  | ENCL. |  |  |  |
| 22.4.9 |  |  |  | Tests of clamping of non-armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tests of clamping of non-armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Allowable cable sizes/size ranges: |  |  |  |  |  |  |  |  |  |  | 1) |  |  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |  |  |  |  |
| Clamping |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| For elastomeric sealing rings: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The sealing ring was mounted on a clean, dry polished, cylindrical mild steel mandrel of a diameter equal to the smallest cable diameter allowable in the ring as specified by the manufacturer of the cable entry. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Mandrel sizes used: |  |  |  |  | 1) |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  |
|  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |
| For metallic sealing rings: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The sealing ring was mounted on the metallic sheath of a sample of clean dry cable of diameter equal to the smallest allowable in the ring as specified by the manufacturer of the cable entry. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable type(s) used: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable sizes used: |  |  |  |  | 1) |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  |
|  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |
| Other sealing methods: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The cable entry was prepared according to the manufacturer's instructions using the prescribed sealing material and sizes of cable samples. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable type(s) used: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable sizes used: |  |  |  | 1) |  |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  |
|  |  |  |  |  | 4) |  |  |  |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |
| Preparation of test samples (cable entry assembly mounted on a tensile test machine): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The sealing ring was compressed while observing in each case the value of tightening torque necessary to prevent slipping of the mandrel or cable with applied force equal to 20 times the value in mm of the mandrel or cable. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Tensile force: |  |  |  |  | 1) |  |  |  |  |  |  | N |  | 2) |  |  |  |  |  | N |  | 3) |  |  |  |  |  | N |  |
|  |  |  |  |  |  | 4) |  |  |  |  |  |  | N |  | 5) |  |  |  |  |  | N |  | 6) |  |  |  |  |  | N |  |
|  | Tightening torque: |  |  |  |  | 1) |  |  |  |  |  |  | Nm |  | 2) |  |  |  |  |  | Nm |  | 3) |  |  |  |  |  | Nm |  |
|  |  |  |  |  |  | 4) |  |  |  |  |  |  | Nm |  | 5) |  |  |  |  |  | Nm |  | 6) |  |  |  |  |  | Nm |  |
| Test procedure: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 110% of the tightening torque determined above was applied to the cable entry clamping screws or nut. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A constant tensile force equal to that defined above was maintained for 6 h. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Slipping of mandrel or cable sample:  6mm is acceptable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | 1) |  |  |  |  |  |  | mm |  | 2) |  |  |  |  |  | mm |  | 3) |  |  |  | mm |  |  |
|  |  |  |  |  |  |  | 4) |  |  |  |  |  |  | mm |  | 5) |  |  |  |  |  | mm |  | 6) |  |  |  | mm |  |  |
| continued on 4/5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 43 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  | SECTION FOUR  VERIFICATIONS AND TESTS 4/5 |  |  |  |  |  |  |  |  |  |  |  |  | APPLIED |  |  |  |  |  |  |  |  |  |  |  |
| ###### CLAUSE |  |  |  | REQUIREMENTS |  |  |  |  |  |  |  |  |  |  |  |  | YES |  |  |  |  | NO |  | ENCL. |  |  |  |  |
| 22.4.9 |  |  |  | Tests of clamping of non-armoured cables in cable entries (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 22.4.10 |  |  |  | ###### Tests of clamping of armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tests of clamping of non-armoured cables in cable entries (continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mechanical strength (Note: The cable entry is removed from the tensile test machine for this test.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Twice the tightening torque that prevents slipping was applied to the cable entry clamping screws or nut. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Results of examination of components (sample dismantled): Required: No noticeable damage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1) |  |  |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3) |  |  |  |  |  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5) |  |  |  |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Note: Sealing ring deformation shall be ignored. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tests of clamping of armoured cables in cable entries |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Allowable cable sizes/size ranges: |  |  |  |  |  |  | 1) |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |  |  |  |  |  |
| Clamping |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A sample of armoured cable of the smallest diameter allowable as specified by the manufacturer of the cable entry was fitted into the clamping device. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable samples; details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Cable sizes used: |  |  |  | 1) |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  |  | 3) |  |  |  |  |  |  |  |
|  |  |  |  |  | 4) |  |  |  |  |  |  | 5) |  |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |
| Preparation of test samples (cable entry assembly mounted on a tensile test machine): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | The clamping device was tightened while observing in each case the value of minimum torque necessary to prevent slipping of the cable with applied force equal to 80 times the value in mm of the cable over the armour. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Tensile force: |  |  |  | 1) |  |  |  |  | N |  |  | 2) |  |  |  |  |  |  | N |  | 3) |  |  |  | N |  |  |
|  |  |  |  |  | 4) |  |  |  |  | N |  |  | 5) |  |  |  |  |  |  | N |  | 6) |  |  |  | N |  |  |
|  | Tightening torque: |  |  |  | 1) |  |  |  |  | Nm |  |  | 2) |  |  |  |  |  | Nm |  |  | 3) |  |  |  |  | Nm |  |
|  |  |  |  |  | 4) |  |  |  |  | Nm |  |  | 5) |  |  |  |  |  | Nm |  |  | 6) |  |  |  |  | Nm |  |
| Test procedure: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A constant tensile force equal to that defined above was maintained for 2 min. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Slipping of the cable armour: Required to be effectively zero |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1) |  |  |  | mm |  |  | 2) |  |  |  |  |  | mm |  |  | 3) |  |  |  | mm |  |  |  |
|  |  |  |  |  | 4) |  |  |  | mm |  |  | 5) |  |  |  |  |  | mm |  |  | 6) |  |  |  | mm |  |  |  |
| Mechanical strength (Note: The cable entry is removed from the tensile test machine for this test.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 2  the tightening torque determined in the clamping test was applied to the cable entry clamping screws or nut. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Results of examination of components (sample dismantled): Required: No noticeable damage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1) |  |  |  |  |  |  |  |  |  |  | 2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3) |  |  |  |  |  |  |  |  |  |  | 4) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5) |  |  |  |  |  |  |  |  |  |  | 6) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 44 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)

| ATTACHMENT B Apparatus for use in zone 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### IEC 60079-0 |  |  |  |  | SECTION FOUR  VERIFICATIONS AND TESTS 5/5 |  |  |  |  |  | APPLIED |  |  |  |  |
| ###### CLAUSE |  |  |  |  | REQUIREMENTS |  |  |  |  |  | YES |  | NO | ENCL. |  |
| 23 |  |  |  |  | Routine verifications and tests |  |  |  |  |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Routine verifications and tests |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: 1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to forms for specific types of protection: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to specification(s) submitted per definitive documents list , Item(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | per established procedure(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: 2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to forms for specific types of protection: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to specification(s) submitted per definitive documents list, Item(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | per established procedure(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: 3) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to forms for specific types of protection: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to specification(s) submitted per definitive documents list, Item(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | per established procedure(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Applied to: 4) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to form(s) for specific type(s) of protection: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | refer to specification(s) submitted per definitive documents list, Item(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | per established procedure(s): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Details: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Sheet 45 of 45 	(IEC 60079-0, 1983, Amendments 1 and 2)