| Reference No: |  |  |  |  |  |  |  |  |  |  |  |  | #### IEC 61241-1 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ## Field of application This form is intended to be used when assessing and testing electrical apparatus for explosive atmospheres according to the standard specified in the adjoining column. The test results are valid for the tested items only. Reproduction This report must not be reproduced other than in its entirety except with the prior written approval of the issuing body |  |  | Standard: # IEC 61241-1: 2004 First Edition Electrical apparatus for use in the presence of combustible dust Part 1: protection by enclosures "tD" |  |  |  |  | ## Instructions for use The comment columns can be used to e.g. specify test values, applied alternative requirements/tests or to refer to enclosed additional pages with comments. Abbreviations: N/A = Not applicable (for the assessment/test of the equipment and its design documentation) The applicant is the body/person who has requested the assessment/test and to which the results, as specified in this report, are provided. The short descriptions in the column for "Clause" do not replace the complete text in the standard. |  |  |  |  |  |  |  |
|  |  |  | Amendments: None |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | # This test report may only be used for the IECEx Scheme and must be accompanied by an ExTR cover page issued by an ExCB. |  |  |  |  |  |  |  |
| ## Product name |  |  |  |  |  |  | # Model/Type designation |  |  |  |  |  |  |  |  |
| Serial No |  | Code (e.g. Ex tD A2_ IP T °C TL °C) (e.g. Ex tD B2_ T °C) |  |  |  |  |  |  | Ambient temperature [min-max] |  |  |  |  |  |  |
| Applicant [name and postal address] |  |  |  |  |  |  | Manufactured by [name and postal address] |  |  |  |  |  |  |  |  |
| Test sample received [date] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ## Product description |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The equipment complies with the standard [yes/no] | ## Prepared by |  |  |  |  |  |  |  |  |  | Date [year-month-day] |  |  |  |  |
|  | [signature] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Reference No: |  |  |  |  |  |  |  |  |  |  |  |  | IEC 61241-1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Clause |  |  |  | Results |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Pass |  | Fail |  | N/A |  | Comments |  |  | ExCB Review |  |
| 1 | Scope |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 | Normative references |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 | Terms and definitions |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 | Construction |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 | Practice A and practice B |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 | Supplementary requirements for electrical apparatus protected by enclosures for practice A for use in zone 20, 21 and 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 | Supplementary requirements for electrical apparatus protected by enclosures for practice B for use in zone 20 or 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.1 | Joints |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.1.1 | Plain joints |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.1.2 | Spigotted joints |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.1.3 | Gasketed joints |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.2 | Operating rods, spindles or shafts |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.2.2 | Running contact seals |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.2.3 | Power shafts |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.2.4 | Operating rods |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7.3 | Clearance of bolts |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 | ### Verification and tests |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.1 | General |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.2 |  | Type tests |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.2.1 |  | Test for dust exclusion by enclosures |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.2.1.1 |  | General |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.2.1.2 |  | Dust-tight apparatus for practice A |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.2.1.3 |  | Dust-protected apparatus for practice A |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.2.1.4 |  | Dust-tight apparatus for practice B |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.2.1.5 |  | Dust protected apparatus for practice B |  |  |  |  |  |  |  |  |  |  |  |  |
| 8.2.2 |  | Thermal tests |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 |  | Marking |  |  |  |  |  |  |  |  |  |  |  |  |
| Sheet 2 of 13 (IEC 61241-1: 2004) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| ##### Section 2 EVALUATION RECORD To be completed by ExTL # IEC 61241-1 : 2004 Electrical apparatus for use un the presence of combustible dust Part 1: protection by enclosures "tD" |  |
| --- | --- |
| ### Report |  |
| Report No. |  |
| Tested by ( + signature) Approved by (+ signature) Date of issue |  |
| Client |  |
| Name Address |  |
| Testing laboratory |  |
| Name Address Testing location |  |
| Test item Standard: IEC 61241-1 Description. Trademark. Model and/or type reference Manufacturer |  |
| Sheet 3 of 13 (IEC 61241-1: 2004) |  |

| Test Item (continued) Rating(s) : Type of transformers (where relevant) Application Protection index Other characteristics Rated ambient temperature Ta (°C) | stationary / portable / hand-held IP |
| --- | --- |
| Other information |  |
| Sheet 4 of 13 (IEC 61241-1: 2004) |  |

| General remarks This evaluation record is not valid unless appended to an IECEx Assessment and Test Report issued by an ExCB, in accordance with IECEx 02. This evaluation record shall not be reproduced except in full without the written approval of the testing laboratory. The test results presented in this evaluation record relate only to the item tested. |  |
| --- | --- |
| Copy of marking plate |  |
| Sheet 5 of 13 (IEC 61241-1: 2004) |  |

# Evaluation Record

| ## IEC 61241-1 |  |  | ##### SECTION ONE  GENERAL 1/3 | ENCL. |  |
| --- | --- | --- | --- | --- | --- |
| CLAUSE |  |  | # REQUIREMENTS |  |  |
| 1 |  |  | ## Scope |  |  |
| Apparatus |  |  |  |  |  |
| Scope |  |  |  |  |  |
| The electrical apparatus defined above is feasible for coverage in accordance with the specific requirements addressed by this part of IEC 61241-0 : |  |  |  |  |  |
|  | YES |  |  |  |  |
|  | NO |  |  |  |  |
|  | Notes: |  |  |  |  |
| Overview: |  |  |  |  |  |
| Sheet 6 of 13 (IEC 61241-1: 2004) |  |  |  |  |  |

| ## IEC 61241-1 |  |  | # SECTION ONE  GENERAL 2/3 | ENCL. |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| ##### CLAUSE |  |  | ##### REQUIREMENTS |  |  |  |
| 2 |  |  | ## Normative References |  |  |  |
| 3 |  |  | Definitions |  |  |  |
| 4 |  |  | Construction |  |  |  |
| Note: The type of protection covered by this part of IEC 61241-0 is dependent on the specific requirements addressed in the forms which follow. |  |  |  |  |  |  |
| Item: |  |  |  |  |  |  |
| Normative References |  |  |  |  |  |  |
| The electrical apparatus has been assessed to the most recent editions of the standards which are referenced and posted as provisions of this part of IEC 61241-0: |  |  |  |  |  |  |
|  | YES |  |  |  |  |  |
|  | NO |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |
| Definitions |  |  |  |  |  |  |
|  | All definitions covered in Clause 3 apply, as noted for the specific requirements herein |  |  |  |  |  |
| Construction (refer to forms Clause 4 of IEC 61241-0) |  |  |  |  |  |  |
|  | Apparatus for use in zone 20 |  |  |  |  |  |
|  | The enclosure is considered as infallible and the fault analysis is only applicable to the electrical circuit |  |  |  |  |  |
| Sheet 7 of 13 (IEC 61241-1: 2004) |  |  |  |  |  |  |

| ## IEC 61241-1 |  |  | # SECTION ONE  GENERAL 3/3 | ENCL. |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ##### CLAUSE |  |  | ##### REQUIREMENTS |  |  |  |  |
| 5 |  |  | ## Practice A and practice B |  |  |  |  |
| 6 |  |  | Supplementary requirements for electrical apparatus protected by enclosure for practice A for use in zone 20, 21 and 22 |  |  |  |  |
| Item: |  |  |  |  |  |  |  |
| Practice A and practice B |  |  |  |  |  |  |  |
| Practice used: |  |  |  |  |  |  |  |
|  | Practice A |  |  |  |  |  |  |
|  | Practice B |  |  |  |  |  |  |
| Supplementary requirements for electrical apparatus protected by enclosures for practice A |  |  |  |  |  |  |  |
|  | Dust-tight enclosures IP6X (for use in zone 20, zone 21 or zone 22 with conductive dust) |  |  |  |  |  |  |
|  | Dust-protected enclosure IP5X (for use in zone 22 with non-conductive dust) |  |  |  |  |  |  |
| Sheet 8 of 13 (IEC 61241-1: 2004) |  |  |  |  |  |  |  |

| ## IEC 61241-1 |  |  |  | # SECTION TWO  CONSTRUCTION 1/2 |  | ENCL. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ##### CLAUSE |  |  |  | ##### REQUIREMENTS |  |  |  |
| 7.1.1 |  |  |  | ## Plain joints |  |  |  |
| 7.1.2 |  |  |  | Spigotted joints |  |  |  |
| 7.1.3 |  |  |  | Gasketed joints |  |  |  |
| Item: |  |  |  |  |  |  |  |
| Plain joints |  |  |  |  |  |  |  |
| Required; Measured. Minimum contact width of the plain joint (mm), W; 5; 22. Maximum allowable clearance between the surfaces of the joint (mm), G; 0.05; 0.22. |
| Note : for widths of joints between 5 mm and 22 mm, the maximum clearance may be increased by 0.01 mm for each millimetre increase in joint width greater than 5 mm. |  |  |  |  |  |  |  |
| Spigotted joints |  |  |  |  |  |  |  |
|  | Axial path (L) greater than 1.2 mm |  |  |  |  |  |  |
|  | Radial path (W) greater than 1.2 mm |  |  |  |  |  |  |
| Required; Measured. Minimum radial section (mm), W; 5; 22. Maximum allowable clearance (mm), G; 0.05; 0.22. |
| Note : for widths of joints between 5 mm and 22 mm, the maximum clearance may be increased by 0.01 mm for each millimetre increase in joint width greater than 5 mm. |  |  |  |  |  |  |  |
| Gasketed joints |  |  |  |  |  |  |  |
| Required; Measured. Maximum opening dimension (mm), O; 305; 915; > 915. Minimum required effective width of gasketed joint (mm), W; 3; 4.8; 9.5. |
| Note : for maximum opening dimensions between 305 mm and 915 mm, the effective width of the gasketed joint shall be increased by 0.003 mm for each millimetre increase in the maximum opening dimension greater than 305 mm. |  |  |  |  |  |  |  |
| Sheet 9 of 13 (IEC 61241-1: 2004) |  |  |  |  |  |  |  |

| ## IEC 61241-1 |  |  |  | # SECTION TWO  CONSTRUCTION 2/2 |  | ENCL. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ##### CLAUSE |  |  |  | ##### REQUIREMENTS |  |  |  |
| 7.2.2 |  |  |  | ## Running contact seals |  |  |  |
| 7.2.3 |  |  |  | Power shafts |  |  |  |
| 7.2.4 |  |  |  | Operating rods |  |  |  |
| 7.3 |  |  |  | Clearance of bolts |  |  |  |
| Item: |  |  |  |  |  |  |  |
| Running contact seals |  |  |  |  |  |  |  |
|  | The equipment meets the design details of power shafts and operating rods |  |  |  |  |  |  |
|  | The equipment meets the tests for dust exclusion by enclosures without the running contact seal installed |  |  |  |  |  |  |
| Running contact seals |  |  |  |  |  |  |  |
| Required; Measured. Minimum length of path for power shafts (mm), L; 12.5; 38.5. Maximum allowable diametrical clearance (mm), D2-D1; 0.26; 0.57. |
| Note : for lengths of path for power shafts between 12.5mm and 38.5 mm, the maximum diametrical clearance may be increased by 0.012 mm for each millimetre increase in the length of path greater than 12.5 mm. |  |  |  |  |  |  |  |
| Operating rods |  |  |  |  |  |  |  |
| Required; Measured. Minimum length of path for operating rods, spindles or shafts (mm), L; 12.5; 25.5. Maximum allowable diametrical clearance (mm), D2-D1; 0.13; 0.21. |
| Note : for lengths of path for operating rods, spindles or shafts between 12.5mm and 25.5 mm, the maximum diametrical clearance may be increased by 0.006 mm for each millimetre increase in the length of path greater than 12.5 mm. |  |  |  |  |  |  |  |
| Clearance of bolts |  |  |  |  |  |  |  |
|  | Max diametrical clearance between the unthreaded shank of the bolt and the hole in the enclosure > 0.26 mm |  |  |  |  |  |  |
|  | Length of path > 12.5 mm |  |  |  |  |  |  |
| Sheet 10 of 13 (IEC 61241-1: 2004) |  |  |  |  |  |  |  |

| ## IEC 61241-1 |  |  |  | # SECTION THREE  VERIFICATION & TESTS 1/2 |  | ENCL. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ##### CLAUSE |  |  |  | ##### REQUIREMENTS |  |  |  |
| 8.1 |  |  |  | ## General |  |  |  |
| 8.2.1.1 |  |  |  | Tests for dust exclusion by enclosures (general) |  |  |  |
| 8.2.1.2 |  |  |  | Dust-tight apparatus for practice A |  |  |  |
| 8.2.1.3 |  |  |  | Dust-protected apparatus for practice A |  |  |  |
| Item: |  |  |  |  |  |  |  |
| General |  |  |  |  |  |  |  |
|  | Verification and testing requirements of IEC 61241-0 done |  |  |  |  |  |  |
| Test for dust exclusion by enclosures (general) |  |  |  |  |  |  |  |
| Level of dust exclusion efficiency used : |  |  |  |  |  |  |  |
|  | Dust-tight enclosures |  |  |  |  |  |  |
|  | Dust protected enclosures |  |  |  |  |  |  |
| Dust-tight apparatus for practice A |  |  |  |  |  |  |  |
|  | Enclosures, including rotating machines, satisfy the requirements for IP6X, as specified in IEC 60529 |  |  |  |  |  |  |
| Dust-protected apparatus for practice A |  |  |  |  |  |  |  |
|  | All enclosures, including rotating machines, satisfy the test and acceptance requirements of IP5X, as specified in IEC 60529 |  |  |  |  |  |  |
| Sheet 11 of 13 (IEC 61241-1: 2004) |  |  |  |  |  |  |  |

| ## IEC 61241-1 |  |  |  | # SECTION THREE  VERIFICATION & TESTS 2/2 |  |  | ENCL. |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ##### CLAUSE |  |  |  | ##### REQUIREMENTS |  |  |  |  |  |
| 8.2.1.4 |  |  |  | ## Dust-tight apparatus for practice B |  |  |  |  |  |
| 8.2.1.5 |  |  |  | Dust-protected apparatus for practice B |  |  |  |  |  |
| 8.2.2 |  |  |  | Thermal tests |  |  |  |  |  |
| 9 |  |  |  | Marking |  |  |  |  |  |
| Item: |  |  |  |  |  |  |  |  |  |
| Dust-tight apparatus for practice B |  |  |  |  |  |  |  |  |  |
| Apparatus; Dust particle size; Number of cycles of heating and cooling (≥ 6); Duration of the test (≥ 30 h); No visible dust entered the enclosure. Passes through a N° 100 sieve; 22% passes through a N° 200 sieve. (x); (x); (x). |
| Note : dust in joints is not considered as a failure |  |  |  |  |  |  |  |  |  |
| Dust-protected apparatus for practice B |  |  |  |  |  |  |  |  |  |
| Apparatus; Dust particle size; Number of cycles of heating and cooling (≥ 2); Duration of the test (≥ 10 h); No visible dust entered the enclosure. Passes through a N° 100 sieve; 22% passes through a N° 200 sieve. (x); (x); (x). |
| Note : dust in joints is not considered as a failure |  |  |  |  |  |  |  |  |  |
| Thermal tests |  |  |  |  |  |  |  |  |  |
| ## Practice A |  |  |  |  |  |  |  |  |  |
|  | The test was carried out as described in 23.4.5 of IEC 61241-0 |  |  |  |  |  |  |  |  |
| ## Practice B |  |  |  |  |  |  |  |  |  |
|  | The test was carried out in accordance with 23.4.5.1 to 23.5.1.3 of IEC 61241-0 |  |  |  |  |  |  |  |  |
|  | The apparatus was covered with the maximum amount of dust that it can retain,or |  |  |  |  |  |  |  |  |
|  | A 12.5 mm thick layer of dust paste was applied to the top of the apparatus |  |  |  |  |  |  |  |  |
| Marking |  |  |  |  |  |  |  |  |  |
|  | Clause 29 of IEC 61241-0 applied; (refer to |  |  |  |  |  |  |  | ) |
|  | Notes: 1. The symbol for the type of protection used shall be “tD”. 2. The zone in which the apparatus can be used is prefixed “A” for Practice A and “B” for Practice B. 3. Practice B does not include the IP rating. |  |  |  |  |  |  |  |  |
| Sheet 12 of 13 (IEC 61241-1: 2004) |  |  |  |  |  |  |  |  |  |

| ## IEC 61241-1 | ##### COMMENTS |  |  |
| --- | --- | --- | --- |
| #### Clause |  | Page |  |
| Sheet 13 of 13 (IEC 61241-1: 2004) |  |  |  |