- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

Title:  ExTAG/660/CD – Draft ExTAG Decision Sheet - Revision of ExTAG DS 2015/014 - Terminal Boxes open to the interior of the motor

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

During the ExTAG 2021 Remote Meeting the decision was taken to circulate ExTAG/660/CD Draft ExTAG Decision Sheet - Revision of ExTAG DS 2015/014 - Terminal Boxes open to the interior of the motor to members inviting input for a revision.

The revision was prepared by SGS Baseefa on behalf of IEC TC31 WG 27.

In accordance with OD 035 this document is issued for a six week comment period.

Please submit comments on this new Draft DS using the comments table, a separate document, by –

202112 22

to

Christine Kane

ExTAG Secretariat

Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-15:2010 IEC 60079-7:2015 | Clause: 8.3 5.2.3 | - Date: 2015 09 15 - Revised July 2021 Originator of proposal: SGS Baseefa on behalf of IEC TC31 WG 27 |
| --- | --- | --- |
| Subject: Terminal Boxes open to the interior of the motor Revision of ExTAG DS 2015/014 Status: Draft | Key words: - Terminal Box - Motor | TC/SC involved: TC31 WG27 Draft Decision Sheet: |
| Question: Do the requirements given in 8.3 of IEC 60079-15:2010 or 5.2.3 of IEC 60079-7:2015 prohibit the use of a terminal box open to the interior of a motor rated 1 kV or greater, provided the interior of the machine has an ingress protection of IP54 or greater? IEC 60079-15, Ed 4: 8.3 Terminal boxes Terminal boxes attached to machines operating at voltages up to 1 kV, may be opened to the interior of the machine, only when the IP rating of the machine is IP44 or higher. The external IP protection of the box shall be not less than IP54, as determined in accordance with IEC 60079-0. IEC 60079-7 Ed 5: 5.2.3 Degrees of protection provided by electrical machines, Level of Protection “ec” The requirements of 4.10 apply, except that terminal boxes attached to electrical machines operating at voltages up to 1 kV, may be opened to the interior of the machine, only when the degree of protection of the electrical machine is at least IP44. Covers and entries of the terminal box shall provide at least degree of protection IP54. Answer: No. As long as the interior of the machine has an ingress protection of IP54 or greater, determined in accordance with IEC 60079-0, there is no limitation to less than 1 kV. If the interior of the machine has an ingress rating of IP44 or lower, the use of a terminal box open to the interior of a motor rated 1 kV or greater is not permitted. NOTE 1: Many manufacturers opt to declare IP44 for the machine for certification purposes, whilst claiming a rating of IP54 or higher, by assessment, for contractual purposes in order to avoid the difficult testing required for certification of the IP of larger machines. As such, this additional IP rating need only comply with IEC 60529 or IEC 60034-5 as applicable, and not with any of the testing detailed in IEC 60079-0. NOTE 2: The initial version of this DS was prepared by TC 31 WG27 at its meeting in Mississauga, following a request for clarification by one of the members of WG27. WG27 subsequently prepared the relevant I-SH and the published I-SH text has been reproduced in this revised ExTAG Decision Sheet. It is compatible with the text currently proposed for Edition Six of IEC 60079-7. |  |  |