### INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

# Title: ExTAG/770/CD, Draft ExTAG Decision Sheet – Application of Standards for Skin-Effect trace heating systems

# Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

# This document, ExTAG/770/CD, Draft ExTAG Decision Sheet - – Application of Standards for Skin-Effect trace heating systems has been prepared by CNEx China, and is issued for consideration by ExTAG.

In accordance with OD 035 this document is issued for a six week comment period.

Please submit comments on this new Draft DS using the online Draft DS Review System – 2026 07 13

ExTAG Secretariat

| Address: Level 17, Angel Place 123 Pitt Street Sydney NSW 2000 Australia | Contact Details: Tel: +61 2 46 28 4690 Fax: +61 2 46 27 5285 e-mail: info@iecex.com http://www.iecex.com |
| --- | --- |

ExTAG/770/CD, Draft ExTAG Decision Sheet – Application of Standards for Skin-Effect trace heating systems

| Standard: IEC 60079-7：2017 IEC 60079-0：2017 IEC/IEEE 60079-30-1 | Clause: 5.8.1， 6.1 | Date: May 2026 |
| --- | --- | --- |
| Subject: - Applicable standards for skin effect trace heating system | Key words: - Skin effect trace heating system - IEC/IEEE 60079-30-1 | Originator of proposal: CNEx |
| Status of document: Draft |  | TC/SC involved: IEC/TC 31 MT 60079-30 |
| Background: IEC 60079-7:2017, Clause 5.8 Resistance Heating (Except Electric Heat Tracing) 5.8.1 General This subclause specifies supplementary requirements for the resistance heating devices and resistance heating units (other than trace heating systems) defined in Clause 3.13. It does not apply to induction heating, skin effect heating, dielectric heating or any other heating system which involves passing current through a liquid, an enclosure or pipe. Note 1: The requirements for electric trace heating systems are provided in IEC 60079-30-1. The applicable IECEx standards for skin effect trace heating systems are not clear enough. |  |  |
| Question: - Is it permitted to use IEC/IEEE 60079-30-1 as the basis for testing and certification of the skin effect trace heating systems? - Is compliance with IEC 60079-0 and IEC 60079-30-1 sufficient for the skin effect trace heating system to obtain IECEx certification? |  |  |
| Answer: - Yes. - No. IEC/IEEE 60079-30-1 does cover such type of products. However, manufacturers need to additionally consider Clause 6.1 of IEC 60079-0 “The requirements of this standard, together with one or more of the specific standards listed in Clause 1, are in addition to the applicable safety requirements of the relevant industrial standards.” |  |  |
| This DS is applicable to: projects commenced prior to publication of the DS; AND all certifications issued after its publication; OR only for the new certifications (Issue No. 0) and their subsequent revisions. |  |  |

NOTE: The following should be noted when developing ExTAG Decision Sheets:

The development process should be in compliance with IECEx OD 035.

The purpose for development of ExTAG Decision Sheets is to unify the application of the Standards used in the IECEx System and is not intended to modify or "interpret" Standards